## ESTIMATE
SCH-3270 ¦ ROM COST ESTIMATE ¦ LEVEL 3 ¦ FY27 ¦ PAX ID 387568 ¦ Fi Web BU26PPE74M
A. ROM FORMULA CHAIN - UFS 3-740-05 LEVEL 3
| Element | Amount ($) | Formula / Source
1 | Base Direct Cost (FY24 CONUS) | 792000 | Sum of all scope items - SCOPE_DETAIL tab
2 | x ACF 1.85 (Camp Schwab) = ACF-Adjusted Cost | 1465200 | C4 x ACF 1.85 per UFC 3-701-01 w/Change 7 (25 Jul 2025), Table 4-1
3 | x Compound Escalation Factor = Escalated Cost (FY27) | 1559459.6288 | C5 x (1.021)^3 = 1.0643 ¦ FY24 to FY27 ¦ OSD FY25 published rate
4 | x (1 + General Requirements 10%) = Gen Req Applied | 1715405.5917 | C6 x 1.10 ¦ General Requirements per UFS 3-740-05
5 | x (1 + Contingency 10%) = Construction Subtotal | 1886946 | ROUND(C7 x 1.10, 0) ¦ Level 3 ROM 10% contingency - FSRM program-directed
6 | + LSH Allowance (2.5% of PRV) | 987690 | PRV $39,507,617 x 2.5% ¦ iNFADS RPUID 1174058 ¦ MCO 11000.12 ¦ NAVFAC 11010.44E CH-1
| CONSTRUCTION BASE (Construction Subtotal + LSH) | 2874636 | Construction Subtotal + LSH Allowance
B. PROGRAM ADDERS
| Element | Amount ($) | Formula / Source
| Design (6.0%) | 172478.16 | Construction Base x 6.0% ¦ NAVFAC agency-directed
| SIOH (8.0% - OCONUS FSRM Customer-Directed) | 229970.88 | Construction Base x 8.0% ¦ OCONUS FSRM customer-directed rate (NOT standard 7.3%)
| Construction Management (4.0%) | 114985.44 | Construction Base x 4.0% ¦ NAVFAC agency-directed
| TOTAL FUNDED COST | 3392070 | Construction Base + Design + SIOH + CM ¦ rounded to nearest dollar
| Design-Build Design (4.0%) - Applied AFTER Total Funded | 135682.8 | Total Funded x 4.0% ¦ UFC 3-730-01 (2024) ¦ applied after Total Funded per DD1391 convention
| TOTAL PROJECT COST | 3527752.8 | Total Funded + Design-Build Design
C. COST PER SQUARE FOOT
| Item | Amount ($) | Basis
| Cost / Whole Building GSF (25,390 SF) | 133.5987 | Total Funded / total building GSF ¦ systems repair benchmark ¦ LSH is dominant driver at this scope level
D. UNIFORMAT II LEVEL 2 SUMMARY - Base Direct Cost (FY24 CONUS Pre-ACF)
Code | Category | Base Direct ($) | Description / Items
B20 | Exterior Doors | 22000 | Roll-up door inspection and repair ¦ 22 EA ¦ 2010 vintage exterior vehicle bay doors
C10 | Interior Construction | 43000 | Wall repair ¦ anchor wire cable resecure ¦ restroom remediation
C30 | Interior Finishes | 17500 | Ceiling tile replacement ¦ 2,500 SF mold/mildew damaged tile
D20 | Plumbing | 18800 | Emergency eyewash/shower stations ¦ 2F water cooler RM214
D30 | HVAC / Mechanical | 504800 | ACP replacement (7 outdoor + 24 fan coils) ¦ DOAS (4 units) ¦ exhaust fans (22 EA) ¦ hose reels (10 EA) ¦ RM117 welding exhaust ¦ RM114 removal ¦ battery room ¦ compressed air
D50 | Electrical / Communications | 185900 | Lighting (94 fixtures) ¦ Cat6 NIPR infrastructure (70 drops) ¦ TR upgrades ¦ MNS
| TOTAL BASE DIRECT COST (FY24 CONUS) | 792000 | Must equal Base Direct C4 exactly - SUMIF verification
E. ESTIMATE VERSION HISTORY
| Estimate Version | Total Funded ($) | Notes
| v8 (07 Mar 2026) | 2374358 | HVAC ACP replacement (7 units + 24 fan coils) + lighting (94 fixtures) + telecom Cat6/WAO infrastructure only
| v9 (19 Mar 2026) - CURRENT | 3392070 | Full mechanical scope added: DOAS (4 units) + exhaust systems (22 fans + 10 hose reels) + welding exhaust restore + battery room + compressed air + plumbing + roll-up doors (22 EA) + NIPR drops (70 EA) + MNS + architectural
| Delta (v9 vs v8) | 1017712 | Scope expansion: full mechanical discipline + communications + architectural
F. METHODOLOGY SUMMARY
| 1. Estimate Level | Level 3 ROM per UFS 3-740-05 (2 Feb 2026), Table 2-1. Non-mandatory supplement; For Information Only. No accuracy percentage ranges cited. Site survey Feb 2026. Mechanical scope confirmed 19 Mar 2026. Communications scope and NIPR requirements confirmed 19 Mar 2026.
| 2. Scope Basis | 42 discrete work items across 10 discipline groups: Mechanical HVAC ACP replacement, DOAS fresh air (4 units), exhaust systems (22 fans + 10 hose reels), battery room, compressed air; Plumbing (safety stations + water cooler); Exterior Doors (roll-up door repair, 22 EA); Electrical lighting (94 fixtures); Communications (Cat6 NIPR infrastructure 70 drops, TR upgrades, MNS); Architectural (ceiling tile, wall repair, restroom remediation). DD Form 1391 PAX ID 387568. iNFADS RPUID 1174058. References: AS-BUILT COMM drawings MC0513T H20 (2008); mechanical as-built drawings reviewed 19 Mar 2026; ACP equipment schedule confirmed 07 Mar 2026.
| 3. Area Cost Factor | 1.85. Camp Schwab, Okinawa, Japan per UFC 3-701-01 w/Change 7 (25 Jul 2025), Table 4-1 OCONUS, installation M67400-0004.
| 4. Escalation | 2.1%/yr; OSD FY25 published rate, client-confirmed. FY24 base to FY27 target = 3 years. Compound factor (1.021)^3 = 1.0643322610 (live formula in PARAMETERS B39).
| 5. General Requirements | 10.0%, FSRM program-directed.
| 6. Contingency | 10.0%, FSRM program-directed, Level 3 ROM. UFS 3-740-05 (2 Feb 2026).
| 7. LSH | PRV = $39,507,617 (iNFADS confirmed ¦ RPUID 1174058 ¦ CCN 21451 ¦ 25,390 GSF). LSH = PRV x 2.5% = $987,690. Authority: NAVFAC 11010.44E CH-1; MCO 11000.12 (08 Sep 2014). LSH represents a significant portion of Total Funded consistent with a targeted systems repair project at a large facility.
| 8. Program Adders | Design 6%, NAVFAC agency-directed. SIOH 8.0% OCONUS FSRM customer-directed (NOT standard 7.3%; deviation documented). CM 4% agency-directed. DB Design 4% applied AFTER Total Funded per UFC 3-730-01 (2024). Delivery method: Design-Build (DB).
| 9. Unit Cost Basis | FY24 CONUS pre-ACF unit costs per RS Means assembly-level data. UFC 3-410-01 (HVAC), UFC 3-520-01 (Electrical), UFC 3-530-01 (Lighting), UFC 3-580-01 (Communications), UFC 3-420-01 (Plumbing). ACP capacities and quantities confirmed from equipment schedule 07 Mar 2026. DOAS unit count (4 EA) and exhaust fan count (22 EA general + 10 hose reels) confirmed from AS-BUILT mechanical equipment schedules. NIPR drops (70 EA: 40 CLB-4 by room, 30 4th MarRegt) confirmed from unit-provided requirements 18 Mar 2026. TR rack infrastructure confirmed from AS-BUILT COMM drawing elevation details. Roll-up door count (22 EA) confirmed from AS-BUILT drawings.
| 10. Items Requiring Verification | JPY/USD exchange rate (PARAMETERS B41): confirm from Federal Reserve H.10 on date of PAX submission.
| 11. Methodology Deviations | iNFADS PRV governs per UFC 3-701-01 w/Change 7 (25 Jul 2025), Section 3-2.1. Formula cross-check: FAC 2141 (Vehicle Maintenance Shop), 25,390 SF x $810/SF (UFC 3-701-01 C7 Table 3, direct read) = $20,565,900; x ACF 1.85 = $38,046,915; x combined factor (HF 1.0 x PD 1.09 x SIOH 1.08 x CF 1.05) = 1.23606; Formula PRV = $47,027,990. iNFADS PRV = $39,507,617. Delta = $7,520,373 (16.0%). Delta is consistent with PUC change cycle; iNFADS valuation predates the current C7 PUC of $810/SF for FAC 2141. Methodolgy: iNFADS-based LSH = $987,690; formula-based LSH = $1,175,700; delta = $188,010; iNFADS governs. GSF: iNFADS 25,390 SF governs. BUILDER records 24,529 SF (861 SF delta). Delta reflects BUILDER net modeled interior footprint vs. iNFADS gross architectural footprint established at asset capitalization. SIOH 8.0% is the FSRM program adder applied to Construction Base; it is separate from and independent of the SIOH factor (1.08) within Equation 3-1 for PRV computation.
| 12. Prepared By | Anthony L. Potter ¦ Facilities Professional ¦ MCIPAC G-F PPE ¦ 19 Mar 2026
| 13. Version History | See Section E above. Current version (v9) Total Funded references live formula =C18. v8 (07 Mar 2026): Total Funded $2,374,358 - initial mechanical scope (ACP units, lighting, telecom). v9 (19 Mar 2026) CURRENT: full mechanical discipline scope added 19 Mar 2026 including DOAS, exhaust systems (22 fans + 10 hose reels), welding exhaust restore, battery room ventilation, compressed air, plumbing, roll-up doors (22 EA), NIPR drops (70 EA), MNS, and architectural items.

## SCOPE_DETAIL
SCH-3270 ¦ SCOPE DETAIL & QUANTITY TAKEOFF ¦ BASE YEAR FY24 CONUS DIRECT COSTS ¦ Fi Web BU26PPE74M
Blue = confirmed scope. Black = formula. All unit costs FY24 CONUS pre-ACF. No HAZMAT scope.
Item | Group | Work Description | Qty | Unit | Unit Cost (FY24 CONUS) | Extended Cost | UNIFORMAT II Lv2 | Cost Basis / Notes
1. MECHANICAL - HVAC ACP SYSTEM REPLACEMENT - 7 Outdoor Units + 24 Indoor Fan Coils + Infrastructure
1 | Mech | Replace VRF outdoor condensing unit ACP-1 ¦ 50.2 KW / 14.3 tons ¦ furnished and installed complete with refrigerant line connections, electrical connections, startup and commissioning | 1 | EA | 23500 | 23500 | D30 | RS Means D3030; large commercial VRF condensing unit; UFC 3-410-01; ACP capacity confirmed 07 Mar 2026
2 | Mech | Replace VRF outdoor condensing unit ACP-2 ¦ 26.2 KW / 7.4 tons ¦ furnished and installed complete | 1 | EA | 14500 | 14500 | D30 | RS Means D3030; UFC 3-410-01
3 | Mech | Replace VRF outdoor condensing unit ACP-3 ¦ 40.0 KW / 11.4 tons ¦ furnished and installed complete | 1 | EA | 19500 | 19500 | D30 | RS Means D3030; UFC 3-410-01
4 | Mech | Replace VRF outdoor condensing unit ACP-4 ¦ 16.0 KW / 4.5 tons ¦ furnished and installed complete | 1 | EA | 10000 | 10000 | D30 | RS Means D3030; UFC 3-410-01
5 | Mech | Replace VRF outdoor condensing unit ACP-5 ¦ 40.0 KW / 11.4 tons ¦ furnished and installed complete | 1 | EA | 19500 | 19500 | D30 | RS Means D3030; UFC 3-410-01
6 | Mech | Replace VRF outdoor condensing unit ACP-6 ¦ 14.0 KW / 4.0 tons ¦ furnished and installed complete | 1 | EA | 9500 | 9500 | D30 | RS Means D3030; UFC 3-410-01
7 | Mech | Replace mini-split condensing unit ACP-7 ¦ 2.2 KW / 0.6 tons ¦ standalone; furnished and installed complete with startup | 1 | EA | 3500 | 3500 | D30 | RS Means D3030; UFC 3-410-01
8 | Mech | Replace indoor VRF fan coil units ACP-3 zone ¦ 14 EA ducted cassette type ¦ mixed 2.2/2.0/2.8 KW ¦ furnished and installed complete | 14 | EA | 2800 | 39200 | D30 | RS Means D3050; qty and capacity confirmed ACP schedule 07 Mar 2026
9 | Mech | Replace indoor VRF fan coil units ACP-4 zone ¦ 3 EA ducted cassette type ¦ mixed 3.6/3.6/1.5 KW ¦ furnished and installed complete | 3 | EA | 2800 | 8400 | D30 | RS Means D3050; qty and capacity confirmed ACP schedule 07 Mar 2026
10 | Mech | Replace indoor VRF fan coil units ACP-5 zone ¦ 4 EA ducted cassette type ¦ mixed 4.5/4.4/6.0/11.2 KW ¦ furnished and installed complete | 4 | EA | 2800 | 11200 | D30 | RS Means D3050; qty and capacity confirmed ACP schedule 07 Mar 2026
11 | Mech | Replace indoor VRF fan coil units ACP-6 zone ¦ 3 EA ducted cassette type ¦ mixed 2.8/2.8/1.45 KW ¦ furnished and installed complete | 3 | EA | 2800 | 8400 | D30 | RS Means D3050; qty and capacity confirmed ACP schedule 07 Mar 2026
12 | Mech | Refrigerant piping ¦ line sets ¦ insulation ¦ fittings ¦ pressure testing ¦ all 7 ACP systems complete | 1 | LS | 20000 | 20000 | D30 | UFC 3-410-01; includes all branch piping to indoor fan coil units
13 | Mech | Electrical disconnects and dedicated circuit connections for 7 outdoor ACP condensing units | 7 | EA | 1800 | 12600 | D30 | UFC 3-520-01; one disconnect and connection set per outdoor ACP unit
14 | Mech | Redesign air pull infrastructure ¦ supply/return vents ¦ fan power boxes ¦ door louvers ¦ 1F and 2F complete | 1 | LS | 18000 | 18000 | D30 | UFC 3-410-01; site survey confirms air pull redesign required throughout building
15 | Mech | Install new split unit HVAC ¦ 1F and 2F hallways ¦ 2 EA ¦ capacity per designer load calculation | 2 | EA | 12000 | 24000 | D30 | RS Means D3030; UFC 3-410-01; new hallway coverage both floors
241800
2. MECHANICAL - DOAS FRESH AIR SYSTEMS - 4 Units + Ductwork Evaluation
16 | Mech | Replace ACP-1 100% outside air packaged unit ¦ RM123 Mechanical Room 3 ¦ serves main shop areas ¦ furnished and installed complete with refrigerant lines, electrical, controls, and startup | 1 | EA | 38000 | 38000 | D30 | RS Means D3060; 100% OA packaged unit; UFC 3-410-01; ASHRAE 62.1; AS-BUILT mech drawings confirmed
17 | Mech | Replace ACP-4-3 outside air processing unit ¦ RM104 Office 1 ¦ furnished and installed complete | 1 | EA | 16000 | 16000 | D30 | RS Means D3060; outside air processing unit; UFC 3-410-01; location confirmed AS-BUILT mech drawings
18 | Mech | Replace ACP-5-4 outside air processing unit ¦ RM207 Class Room ¦ furnished and installed complete | 1 | EA | 16000 | 16000 | D30 | RS Means D3060; UFC 3-410-01; location confirmed AS-BUILT mech drawings
19 | Mech | Replace ACP-6-3 outside air processing unit ¦ RM116 Office 2 ¦ furnished and installed complete | 1 | EA | 16000 | 16000 | D30 | RS Means D3060; UFC 3-410-01; location confirmed AS-BUILT mech drawings
20 | Mech | Existing supply ductwork evaluation and replacement as required ¦ all 4 DOAS systems ¦ designer to confirm reuse vs. replacement per field assessment | 1 | LS | 18000 | 18000 | D30 | UFC 3-410-01; ASHRAE 62.1; ductwork shown in AS-BUILT drawings; reuse determination by designer
104000
3. MECHANICAL - EXHAUST SYSTEMS - 22 General Fans + 10 Hose Reels + Welding Exhaust Restore + RM114 Removal
21 | Mech | Replace general exhaust fans building-wide ¦ 22 EA ¦ FE-1,7,9,10,11,15,16,17 (restroom/shower/janitor) ¦ FE-2,3,4 (storage/recycle) ¦ FE-5,6,12 (shop) ¦ FE-18,19,20,21,FS-1 (mechanical/battery/boiler) ¦ FE-22,33,34 (bay/roof) ¦ furnished and installed complete ¦ designer evaluates duct reuse per room | 22 | EA | 3000 | 66000 | D30 | RS Means D3090; UFC 3-410-01; 2010 vintage approaching EOL; quantities confirmed from mechanical equipment schedule FE-1 through FS-1
22 | Mech | Replace vehicle exhaust hose reel assemblies ¦ 10 EA total ¦ FE-23 through FE-28 in RM105 Maintenance Bay (6 EA) ¦ FE-29 through FE-32 in RM113 Maintenance Bay (4 EA) ¦ fan, reel assembly, and branch duct replacement complete ¦ main exhaust header evaluation included | 10 | EA | 5000 | 50000 | D30 | RS Means D3090; vehicle exhaust capture systems; UFC 3-410-01; quantities and locations confirmed from AS-BUILT mechanical drawings
23 | Mech | Full removal of abandoned dust collection system RM114 Wood Shop ¦ exterior DC unit ¦ wall penetration ¦ all internal ductwork ¦ 4 equipment connection points (miter saw, band saw, table saw, radial saw/sander) ¦ debris disposal complete | 1 | LS | 8500 | 8500 | D30 | RS Means D3090 demolition; UFC 3-410-01; full system extent confirmed from AS-BUILT mechanical drawings
24 | Mech | Repair and restore RM117 Welding Shop exhaust system ¦ replace exhaust fans FE-13 and FE-14 ¦ replace roof ventilator FA-1 ¦ repair/replace welding exhaust hood and all associated ductwork ¦ system originally designed for welding operations and has fallen into disrepair | 1 | LS | 14000 | 14000 | D30 | RS Means D3090; UFC 3-410-01; system fully shown in AS-BUILT drawings as active design; confirmed repair required 19 Mar 2026
138500
4. MECHANICAL - BATTERY ROOM - RM102 Ventilation and Conditioning Upgrade
25 | Mech | Battery room RM102 ventilation and conditioning upgrade ¦ extend multizone split system to meet temperature requirements ¦ upgrade existing wall exhaust fan FE-20 to code-compliant interlocked exhaust for hydrogen gas control ¦ no existing hood or ductwork present | 1 | LS | 12000 | 12000 | D30 | RS Means D3090/D5030; OSHA 1910.178(g); UFC 3-520-01; existing FE-20 wall propeller fan confirmed from AS-BUILT drawings; no duct or hood present
12000
5. MECHANICAL - COMPRESSED AIR - RM119 System Inspection and Repair
26 | Mech | Compressed air system inspection, pressure testing, and repair as necessary ¦ COM-1 compressor and air receiver in RM119 Mechanical Room 1 ¦ full distribution loop through RM105, RM113, and shops RM101-104 ¦ column-mounted air outlet drops throughout | 1 | LS | 8500 | 8500 | D30 | RS Means D3090; system extent and layout confirmed from AS-BUILT compressed air plan drawings; repair as necessary
8500
6. PLUMBING - Safety Stations and Fixtures
27 | Plmb | Replace emergency eyewash and shower stations building-wide ¦ replace 4 EA E-2 eyewash stations (2x RM102 Battery Room, 2x RM105 Maintenance Bay) ¦ replace 1 EA E-1 combo shower/eyewash in RM102 ¦ add 2 emergency shower stations at RM105 locations currently equipped with eyewash only ¦ all per ANSI Z358.1 distance requirements | 1 | LS | 16000 | 16000 | D20 | RS Means D2010; ANSI Z358.1; UFC 3-420-01; fixture locations and types confirmed from AS-BUILT plumbing drawings
28 | Plmb | Replace 2F electric water cooler ¦ RM214 corridor ¦ EW-1 fixture tag ¦ furnished and installed complete | 1 | EA | 2800 | 2800 | D20 | RS Means D2020; UFC 3-420-01; fixture location confirmed from AS-BUILT plumbing drawings
18800
7. EXTERIOR DOORS - Roll-Up Door Inspection and Repair
29 | Arch | Inspect and repair overhead roll-up doors ¦ 22 EA total ¦ RM105 (6 front, 6 rear) ¦ RM113 (3 front, 3 rear) ¦ wing rooms 101-104 (1 EA each, 4 total) ¦ check springs, cables, operators, seals, and tracks ¦ repair as necessary ¦ all 2010 vintage | 22 | EA | 1000 | 22000 | B20 | RS Means G2050; 2010 vintage exterior vehicle bay doors; quantity and locations confirmed from AS-BUILT drawings; UNIFORMAT B2030 Exterior Doors
22000
8. ELECTRICAL - LIGHTING REPLACEMENT - 94 Confirmed Fixtures + Motion Sensors
30 | Elect | Replace high bay fixtures ¦ F-8-322-PH26 (4 EA pipe pendant) ¦ F-11-321-PH26 (2 EA wall) ¦ F-16-321-PH26 (15 EA recessed) ¦ F-16-322-PH26 (1 EA recessed) ¦ L-2-J13-16 (18 EA recessed) ¦ L-0-J13-10 (2 EA pendant) ¦ F-20-ST1FRF22P-C (2 EA recessed) ¦ F-22-SHI-FBC20-C (18 EA wall) ¦ 62 EA total ¦ furnished and installed | 62 | EA | 650 | 40300 | D50 | RS Means D5020; UFC 3-530-01; fixture schedule confirmed 05 Mar 2026
31 | Elect | Replace 400W metal halide high bay fixtures SP3-HSR1M-400BH26 ¦ ceiling mounted ¦ 30 EA ¦ lift and rigging required ¦ furnished and installed | 30 | EA | 1800 | 54000 | D50 | RS Means D5020; UFC 3-530-01; fixture schedule confirmed 05 Mar 2026
32 | Elect | Replace 400W metal halide fixtures SP-2 HSR1M-400BH26 with integrated optical sensors ¦ 2 EA ¦ coordinate with fire detection system prior to execution | 2 | EA | 3200 | 6400 | D50 | UFC 3-530-01; NFPA 72; fire detection system coordination required before execution
33 | Elect | Replace motion sensor lighting fixtures ¦ qty and fixture type per full 1F and 2F lighting survey ¦ includes wiring and switch leg modifications | 1 | LS | 14000 | 14000 | D50 | RS Means D5020; UFC 3-530-01; full lighting survey to be conducted during design phase
34 | Elect | Electrical panel work ¦ circuit modifications ¦ branch wiring associated with fixture replacement throughout 1F and 2F | 1 | LS | 10000 | 10000 | D50 | UFC 3-520-01; includes panel schedule updates and circuit documentation
124700
9. COMMUNICATIONS - Cat6 NIPR Infrastructure + MNS - 70 Drops + Both TRs
35 | Comm | Remove existing Cat5 and Cat3 cabling building-wide ¦ 1F and 2F ¦ includes J-boxes ¦ patch panels ¦ abandoned cable ¦ complete | 1 | LS | 7500 | 7500 | D50 | UFC 3-580-01; building-wide removal required prior to new Cat6 installation
36 | Comm | Install Cat6 structured cabling infrastructure ¦ 70 NIPR drops total ¦ 40 EA CLB-4 (by room per unit-provided requirements 18 Mar 2026) ¦ 30 EA 4th Marine Regiment (opposite side of building) ¦ horizontal runs to 1F TR and 2F TR ¦ Cat6 cable ¦ EMT conduit ¦ J-boxes ¦ WAOs ¦ terminations and labeling ¦ both TRs complete | 70 | EA | 210 | 14700 | D50 | RS Means D5030; UFC 3-580-01; TIA-568; NIPR requirements confirmed by unit 18 Mar 2026
37 | Comm | TR infrastructure upgrade ¦ replace patch panel assemblies, switching hubs, and 110-blocks in both 1F TR and 2F TR ¦ rack work ¦ labeling ¦ testing complete ¦ both TRs sized to support 70-drop Cat6 infrastructure | 2 | EA | 8500 | 17000 | D50 | RS Means D5030; UFC 3-580-01; TR rack infrastructure and port density confirmed from AS-BUILT COMM drawings TR elevation details; both TRs accessed 14 Mar 2026
38 | Comm | Install MNS junction box and Mass Notification System infrastructure building-wide | 1 | LS | 22000 | 22000 | D50 | RS Means D5030; UFC 3-580-01; MNS scope confirmed as required
61200
10. ARCHITECTURAL - Interior Repairs and Remediation
39 | Arch | Replace mold and mildew damaged ceiling tile ¦ building-wide assessment ¦ replacement as required | 2500 | SF | 7 | 17500 | C30 | RS Means C3020; UFC 3-410-01; documented mold/mildew deficiency confirmed site survey
40 | Arch | Repair gypsum and concrete wall damage throughout building ¦ patch and repair ¦ painted finish to match | 1 | LS | 20000 | 20000 | C10 | RS Means C1020; documented deficiency confirmed site survey
41 | Arch | Resecure anchor wire cables to exterior HVAC units ¦ all units ¦ hardware replacement as needed | 1 | LS | 8000 | 8000 | C10 | RS Means G2090; exterior ACP unit anchor wire cable deficiency confirmed site survey
42 | Arch | Deep clean all restrooms ¦ mold and mildew remediation ¦ surfaces, fixtures, and drain areas complete | 1 | LS | 15000 | 15000 | C10 | RS Means Z0040; documented mold/mildew remediation requirement confirmed site survey
60500
TOTAL BASE DIRECT COST (FY24 CONUS) | [5 empty] | 792000

## PARAMETERS
SCH-3270 ¦ COST ESTIMATE PARAMETERS ¦ LEVEL 3 ROM ¦ FY27 ¦ PAX ID 387568 ¦ Fi Web BU26PPE74M
PROJECT IDENTIFICATION
Parameter | Value | Unit | Source / Authority
Estimate Title | SCH-3270 Repair Mechanical / Electrical / Communications / Architectural | Text | DD Form 1391 ¦ PAX ID 387568 ¦ Fi Web BU26PPE74M
Building / Installation | SCH-3270 ¦ Camp Schwab, Okinawa, Japan | Text | MCIPAC G-F PPE
Supported Units | 4th Marine Regiment ¦ CLB-4 | Text | Primary: 4th MAR REGT ¦ Secondary: CLB-4
PAX ID | 387568 | ID | PAX System
Fi Web Project Number | BU26PPE74M | ID | Fi Web - confirmed
Primary Project CCN | 21451 | CCN | CCN 21451 ¦ Auto Organizational Shop ¦ FAC 2141
Estimate Date | 19 Mar 2026 | Date | Date of estimate production
Estimate Level | Level 3 ROM | UFS 3-740-05 | Accuracy range not cited; For Information Only
Delivery Method | Design-Build (DB) | Method
COST INPUTS (Blue = user input)
Parameter | Value | Unit | Source / Authority
Base Year | 2024 | FY | FY24 CONUS base costs
Target Fiscal Year | 2027 | FY | FY27 construction start
Area Cost Factor (ACF) | 1.85 | Multiplier | UFC 3-701-01 w/Change 7 (25 Jul 2025), Table 4-1 OCONUS, M67400-0004
Escalation Rate (annual) | 2.1% | % | OSD FY25 published rate, client-confirmed; applies FY24 through FY27
Escalation Years | 3 | Years | FY24 base to FY27 target = 3 years
General Requirements | 10% | % | FSRM program-directed; UFC 3-701-01
Contingency Rate | 10% | % | Level 3 ROM - FSRM program-directed rate
LSH Rate | 2.5% | % | NAVFAC 11010.44E CH-1 ¦ MCO 11000.12 (08 Sep 2014)
Design Rate | 6% | % | NAVFAC agency-directed - 6%
SIOH Rate | 8% | % | OCONUS FSRM customer-directed rate - 8.0% (NOT standard 7.3%)
Construction Management (CM) | 4% | % | NAVFAC agency-directed - 4%
Design-Build Design | 4% | % | Applied AFTER Total Funded per UFC 3-730-01 (2024)
AREA (GSF) AND UFC UNIT COSTS
Parameter | Value | Unit | Source / Authority
Total Building GSF | 25390 | SF | iNFADS confirmed ¦ Floor 1: 20,672 SF ¦ Floor 2: 4,718 SF ¦ CCN 21451
RPUID | 1174058 | ID | iNFADS ¦ Camp Schwab ¦ CCN 21451 ¦ authoritative per DoW real property records
Plant Replacement Value (PRV - iNFADS) | 39507617 | $ | iNFADS RPUID 1174058 ¦ confirmed ¦ PRV taken directly; not computed via formula for this building
LSH Allowance (2.5% of PRV) | 987690 | $ | PRV x 2.5% ¦ MCO 11000.12 (08 Sep 2014) ¦ NAVFAC 11010.44E CH-1
PUC (FAC 2141, CCN 21451 - Vehicle Maintenance Shop) | 810 | $/SF | UFC 3-701-01 w/Change 7 (25 Jul 2025), Table 3, direct read ¦ GUC: Military Vehicle Maintenance Small (<21,000 SF)
DERIVED VALUES (Formula-driven - do not edit)
Parameter | Value | Unit | Formula Basis
Compound Escalation Factor | 1.0643 | Factor | (1 + 0.021)^3 = 1.0643322610 ¦ live formula
JPY/USD Exchange Rate |  | Rate | CONFIRM from Federal Reserve H.10 on date of PAX submission ¦ JPY column is display-only; ROM chain is USD only
KEY NOTES
Escalation: OSD FY25 published rate 2.1%/yr confirmed. FY26/FY27 same rate applies per client direction.
SIOH: 8.0% is the customer-directed OCONUS FSRM rate for MCIPAC G-F. This is NOT the standard OCONUS rate of 7.3%.
Contingency: 10% is the FSRM program-directed rate for Level 3 ROM. Authority: UFS 3-740-05 (2 Feb 2026).
DB Design (4%) is applied AFTER Total Funded Cost per UFC 3-730-01 (2024). Delivery method: Design-Build (DB).
PRV taken directly from iNFADS ($39,507,617 ¦ RPUID 1174058). LSH = $987,690. PRV not computed via UFC formula for this building. Formula cross-check documented in ESTIMATE Section F Item 11.

## DD1391_BLOCK9
SCH-3270 ¦ COST ESTIMATE PARAMETERS ¦ LEVEL 3 ROM ¦ FY27 ¦ PAX ID 387568 ¦ Fi Web BU26PPE74M
All amounts in $000s per DD Form 1391 convention. All formulas reference ESTIMATE tab. Carry to dollar; round only here.
Cost Element | Amount ($000s) | Notes
1. Exterior Doors - Roll-up door inspection and repair (22 EA) | 47.65 | Roll-up doors (B20) ¦ 22 EA exterior vehicle bay doors ¦ 2010 vintage
2. Interior Construction - Wall repair, anchor wire cables, restroom remediation | 93.134 | Interior construction repairs (C10) ¦ 3 architectural scope items
3. Interior Finishes - Ceiling tile replacement (2,500 SF) | 37.904 | Interior finishes (C30) ¦ mold/mildew ceiling tile replacement
4. Plumbing - Emergency safety stations and 2F water cooler | 40.719 | Plumbing (D20) ¦ eyewash/shower stations + water cooler RM214
5. Mechanical HVAC - ACP replacement, DOAS, exhaust systems, battery room, compressed air | 1093.354 | HVAC/Mechanical (D30) ¦ 27 scope items ¦ ACP, DOAS, exhaust, battery room, compressed air
6. Electrical / Communications - Lighting, Cat6 NIPR drops, TR upgrades, MNS | 402.644 | Electrical/Communications (D50) ¦ lighting 94 fixtures ¦ Cat6 70 drops ¦ TR upgrades ¦ MNS
Subtotal (Base Direct x ACF x Escalation x General Requirements) | 1715.4056 | From ESTIMATE tab C7 - pre-contingency subtotal
Contingency (10.0%) - Level 3 ROM, FSRM Program-Directed | 171.5406 | 10% of Gen Req-applied subtotal (row 10) ¦ FSRM program-directed
Life Safety and Health (LSH) - 2.5% of PRV | 987.69 | PRV = $39,507,617 ¦ iNFADS RPUID 1174058 ¦ MCO 11000.12 ¦ NAVFAC 11010.44E CH-1
Design (6.0%) - Applied to Construction Base | 172.4782 | 6.0% of Construction Base ¦ NAVFAC agency-directed
SIOH (8.0%) - OCONUS FSRM Customer-Directed Rate | 229.9709 | 8.0% of Construction Base ¦ OCONUS FSRM customer-directed (NOT standard 7.3%)
Construction Management (4.0%) | 114.9854 | 4.0% of Construction Base ¦ NAVFAC agency-directed
TOTAL FUNDED COST | 3392.07 | Construction Base + Design + SIOH + CM
CLASSIFICATION OF WORK
Construction | 3392.07 | 100% of Total Funded ¦ 10 U.S.C. Section 2802
Special Interest: Restoration and Modernization | 3392.07 | 100% SRM ¦ MCO 11000.12 ¦ DoD 4270.5-M
Design-Build Design (4.0%) - Applied AFTER Total Funded | 135.6828 | UFC 3-730-01 (2024) ¦ DB design applied after Total Funded per DD Form 1391 convention
TOTAL PROJECT COST | 3527.7528 | Total Funded + Design-Build Design
LOCKED PARAMETERS (DO NOT CHANGE WITHOUT DIRECTION)
ACF |  | 1.85 - Camp Schwab per UFC 3-701-01 w/Change 7 (25 Jul 2025), Table 4-1, M67400-0004
Escalation |  | 2.1%/yr ¦ FY24 to FY27 ¦ (1.021)^3 = 1.0643 ¦ OSD FY25 published rate
General Requirements |  | 10.0% ¦ FSRM program-directed
Contingency |  | 10.0% ¦ FSRM program-directed ¦ Level 3 ROM
SIOH |  | 8.0% ¦ OCONUS FSRM customer-directed (NOT standard 7.3%)
Design |  | 6.0% ¦ NAVFAC agency-directed ¦ applied to Construction Base
CM |  | 4.0% ¦ NAVFAC agency-directed ¦ applied to Construction Base
DB Design |  | 4.0% ¦ Total Funded ¦ applied AFTER Total Funded ¦ UFC 3-730-01 (2024)
Delivery Method |  | Design-Build (DB)