## ESTIMATE
SCH-3237 ¦ ROM COST ESTIMATE ¦ LEVEL 3 ¦ FY27 ¦ PAX ID 387622 ¦ Fi Web BU26PPE73M
A. ROM FORMULA CHAIN (live formulas reference PARAMETERS tab)
Step | Element | Amount ($) | Formula / Source
1 | Base Direct Cost (FY24 CONUS) |  | Sum of all scope items on SCOPE_DETAIL
2 | x ACF 1.85 (Camp Schwab Okinawa) |  | UFC 3-701-01 w/Ch 7 (25 Jul 2025), Table 4-1
3 | x Compound Escalation Factor |  | OSD FY25 published rate; FY24 to FY27
4 | x (1 + General Requirements 10%) |  | FSRM program-directed; UFS 3-740-05
5 | x Cost Adjustment Factor (calibrated) |  | Calibrates ROM chain to locked TPC; absorbs base-cost adjustments
| ITEMS SUBTOTAL (PAX Block 9 paste total) |  | Equals Locked TPC / 1.23552
B. PAX ROLLUP VERIFICATION (mirrors what PAX prints on the form)
Step | Element | Amount ($) | Formula / Source
| Items Subtotal |  | From Section A
| + Contingency (10.0%) PAX-applied |  | FSRM program-directed
Items Subtotal x 1.10
| + SIOH (8.0%) PAX-applied |  | OCONUS FSRM customer-directed
TCC x 1.08
| + DB Design (4.0%) PAX-applied |  | UFC 3-730-01 (2024)
TFC x 1.04
| TOTAL PROJECT COST ($000 rounded) |  | Printed face value on DD Form 1391
| Locked TPC ($000 rounded) |  | Reconciliation target
| Reconciliation (must equal 0) |  | Printed minus Locked
| Planning and Design (6.0%) NON ADD |  | Informational; does not roll into TPC
C. UNIFORMAT II LV2 SUMMARY (Base Direct pre-ACF, by category)
Code | Category | Base Direct ($) | Description
C10 | Interior Construction |  | 5 scope item(s)
D30 | HVAC / Mechanical |  | 1 scope item(s)
D50 | Electrical / Communications |  | 4 scope item(s)
F10 | Hazardous Material Abatement |  | 5 scope item(s)
TOTAL BASE DIRECT (must equal Section A row 5)
D. METHODOLOGY
Estimate Level | Level 3 ROM per UFS 3-740-05 (02 Feb 2026). Non-mandatory supplement; for information only.
Scope Basis | 15 discrete work items across 4 UNIFORMAT II Lv2 categories. Quantities and unit costs derived from site survey and AS-BUILT drawings.
Area Cost Factor | 1.85; Camp Schwab Okinawa Japan; UFC 3-701-01 w/Ch 7 (25 Jul 2025), Table 4-1 OCONUS, M67400-0004.
Escalation | 2.1%/yr; OSD FY25 published rate, client-confirmed; FY24 base to FY27 target; compound factor (1.021)^3 = 1.0643.
General Requirements | 10.0%; FSRM program-directed; UFS 3-740-05.
PAX Associated Costs | Contingency 10%, SIOH 8% (OCONUS FSRM customer-directed), DB Design 4%; combined multiplier 1.23552. Planning and Design 6% NON ADD; informational only.
Cost Adjustment Factor | Live formula in PARAMETERS reconciles the ROM chain to the locked Total Project Cost. The factor absorbs base-cost adjustments distributed pro-rata across discipline rollups.
Unit Cost Basis | FY24 CONUS pre-ACF assembly-level unit costs per RS Means; UFC 3-410-01 / 3-420-01 / 3-520-01 / 3-530-01 / 3-580-01 as applicable.
Items Requiring Verification | JPY/USD exchange rate per Federal Reserve H.10 on date of PAX submission.
Prepared By | Anthony L. Potter ¦ Facilities Planner ¦ MCIPAC G-F PPE ¦ 29 Apr 2026
E. VERSION HISTORY
Version | Date | Total Project Cost ($) | Notes
Current | 29 Apr 2026 |  | 4-tab discipline-rollup architecture; PAX-pasteable Block 9; reconciles to locked TPC

## SCOPE_DETAIL
SCH-3237 ¦ SCOPE DETAIL & QUANTITY TAKEOFF ¦ BASE YEAR FY24 CONUS DIRECT COSTS ¦ Fi Web BU26PPE73M
Yellow = confirmed scope. White = formula-driven extended cost. All unit costs are FY24 CONUS pre-ACF, assembly-level RS Means basis.
Item | Group | Work Description | Qty | Unit | Unit Cost (FY24 CONUS) | Extended Cost | UNIFORMAT II Lv2 | Cost Basis / Notes
1. STORAGE RECONFIGURATION - Remove/Replace Floor-to-Ceiling Wire Mesh Cage Partitions, Room 101
1 | STORAGE | Remove existing floor-to-ceiling wire mesh cage partitions, Room 101 (full bay); includes disconnect, demo, and haul-off | 1 | LS | 5000 |  | C10 | YELLOW - cage LF qty and layout unconfirmed; pending Markon floor plan field verification; UFC 3-580-01
2 | STORAGE | Install new floor-to-ceiling wire mesh cage partitions, Room 101; 3 tenant zones: CLB-4 / HQ 4th MAR REGT / UDP (4th Marines); includes framing, hardware, and seismic anchoring | 1 | LS | 25000 |  | C10 | YELLOW - zone dimensions and total LF unconfirmed; pending unit layout confirmation and design
2. TELECOMMUNICATIONS ROOM - INTERIOR CONSTRUCTION - New TR per UFC 3-580-01 (21 Nov 2024) Para 2-3.1.2.2 & MCIPAC G-6 Policy Ltr 03-2024
3 | TR-ARCH | Construct new TR interior partition walls; light gauge metal framing, 5/8 in Type X gypsum board, fire-rated; room sized at approx 1.1 pct of 19,304 SF served area per UFC 3-580-01 Para 2-3.1.2.2(c); no suspended ceiling per Para 2-3.1.2.3 | 1 | LS | 12000 |  | C10 | UFC 3-580-01 Para 2-3.1.2.2 & 2-3.1.2.3; NFPA 101; min room size 10 ft-6 in x 9 ft for bldgs >5,000 SF
4 | TR-ARCH | Install 3/4 in A-C plywood backboards (fire-retardant treated); cover three walls; 8 ft high; grade-A surface exposed; per MCIPAC G-6 Policy Ltr 03-2024 Sec 4(c)(4) | 1 | LS | 3600 |  | C10 | MCIPAC G-6 Policy Ltr 03-2024 Sec 4(c)(4); UFC 3-580-01
5 | TR-ARCH | Install fire-rated door (min 36 in x 80 in); outswing; combination type lock; holds open unassisted; no threshold; per UFC 3-580-01 Para 2-3.1.2.4 and MCIPAC G-6 Policy Ltr 03-2024 Sec 4(c)(3) | 1 | EA | 2500 |  | C10 | UFC 3-580-01 Para 2-3.1.2.4; MCIPAC G-6 Policy Ltr 03-2024 Sec 4(c)(3); NFPA 101
3. TELECOMMUNICATIONS ROOM - HVAC - Dedicated A/C per UFC 3-580-01 Para 2-3.1.3.3 & 2-3.1.3.4
6 | TR-HVAC | Install dedicated mini-split A/C unit (1.5-ton); independent 24/7/365 thermostat; NOT on building time clock or setback; positive atmospheric pressure; space and power capacity for one additional identical unit per Para 2-3.1.3.4(d) (load calculated at <1 ton); includes refrigerant line, condensate, electrical connection | 1 | EA | 4500 |  | D30 | UFC 3-580-01 Para 2-3.1.3.3 & 2-3.1.3.4(d); TIA-569; ASHRAE Class B; UFC 3-410-01
4. TELECOMMUNICATIONS ROOM - ELECTRICAL - Dedicated Panel and Wiring per UFC 3-580-01 Para 2-3.1.3.2
7 | TR-ELEC | Install dedicated electrical branch circuit panel board; 100A min bus; 120/208V 3-phase; 24-space; feed all TR loads from dedicated panel per UFC 3-580-01 Para 2-3.1.3.2; includes panel, breakers, grounding | 1 | EA | 3500 |  | D50 | UFC 3-580-01 Para 2-3.1.3.2; MCIPAC G-6 Policy Ltr 03-2024 Sec 4(c)(6)(a); NEC
8 | TR-ELEC | Install 125V 20A duplex convenience receptacles at 6 ft on-center intervals around TR perimeter walls; twist-lock type receptacles fed from dedicated circuits at each rack/cabinet per UFC 3-580-01 Para 2-3.1.3.2; includes wiring and conduit | 1 | LS | 2000 |  | D50 | UFC 3-580-01 Para 2-3.1.3.2; MCIPAC G-6 Policy Ltr 03-2024 Sec 4(c)(6)(c)(d); NEC
9 | TR-ELEC | Install overhead cable tray system (slotted bottom); sized for 50 pct fill ratio; extend along three walls above equipment cabinets per MCIPAC G-6 Policy Ltr 03-2024 Sec 4(c)(8)(a); includes waterfalls, supports, bonding | 1 | LS | 1500 |  | D50 | MCIPAC G-6 Policy Ltr 03-2024 Sec 4(c)(8)(a); UFC 3-580-01; TIA-569
5. COMMUNICATIONS INFRASTRUCTURE MODERNIZATION - Full Facility Scope per MCIPAC G-6 Policy Ltr 03-2024 & UFC 3-580-01 (21 Nov 2024)
10 | COMM | Communications infrastructure modernization - full facility scope: (1) remove and dispose non-EMT conduit (full facility); (2) install EMT conduit; (3) Cat 6 UTP NIPR (green) and SIPR (red in EMT) cabling; (4) WAO installation (min 2-port per location; 450mm AFF NIPR / 950mm AFF SIPR); (5) new enclosed mesh TR cabinet seismic Zone 4 anchored (4x 1/2 in bolts); (6) patch panels + cable management (WAOs + 25 pct expansion); (7) relocate existing rack from open admin office to new TR; (8) cable testing and test report. Comm engineer preliminary ROM. | 1 | LS | 100000 |  | D50 | YELLOW - comm engineer ROM $100,000 based on available info; additional site survey required (unit items impeded TR access during initial survey); MCIPAC G-6 Policy Ltr 03-2024 Sec 4(b)(c)(f)(g); UFC 3-580-01
6. HAZMAT - ACM MASTIC ABATEMENT - Bhate Environmental Survey 11/29/2001 (NVLAP accredited, Lab: Analytica Solutions)
11 | HAZMAT | ACM abatement mobilization, containment setup, and demobilization; OSHA 29 CFR 1926.1101 compliant; licensed OCONUS contractor | 1 | LS | 5000 |  | F10 | OSHA 1926.1101; 40 CFR Part 61 NESHAP; abatement required prior to slab penetrations (seismic anchors, TR construction)
12 | HAZMAT | ACM mastic abatement (H2 - brown floor tile mastic, 5 pct Chrysotile); Room 101 (main warehouse bay) and interior hallway; floor penetrations for cage seismic anchors and TR construction trigger OSHA 1926.1101 disturbance threshold. | 5590 | SF | 8 |  | F10 | YELLOW - PWD ENV confirmation pending: flooring in Room 101/hallway may have been replaced since 2001 Bhate survey; if mastic removed in prior replacement, scope reduces; Bhate Environmental Survey 11/29/2001, Sample H2, PA Form confirmed
13 | HAZMAT | ACM waste disposal - licensed OCONUS facility; bagged and labeled per OSHA 1926.1101; manifest documentation | 1 | LS | 3000 |  | F10 | OSHA 1926.1101; 40 CFR Part 61 NESHAP; OCONUS disposal surcharge included in unit rate
14 | HAZMAT | Industrial hygienist air monitoring - pre-abatement, continuous during abatement, post-abatement; OSHA personal air sampling | 1 | LS | 4000 |  | F10 | OSHA 1926.1101; standard OCONUS IH monitoring package
15 | HAZMAT | Clearance testing and documentation; final air samples; written clearance report; all required regulatory submittals | 1 | LS | 2000 |  | F10 | OSHA 1926.1101; EPA NESHAP; 40 CFR Part 61
TOTAL BASE DIRECT COST (FY24 CONUS)

## PARAMETERS
SCH-3237 ¦ COST ESTIMATE PARAMETERS ¦ LEVEL 3 ROM ¦ FY27 ¦ PAX ID 387622 ¦ Fi Web BU26PPE73M
PROJECT IDENTIFICATION
Estimate Title | SCH-3237 ¦ Repair WAREHOUSE/ARMORY | Text | DD Form 1391 ¦ PAX ID 387622 ¦ Fi Web BU26PPE73M
Building / Installation | SCH-3237 ¦ Camp Schwab, Okinawa, Japan | Text | MCIPAC G-F PPE
Supported Units | 4th Marine Regiment / III MEF | Text | Primary supported units
PAX ID | 387622 | ID | PAX System
Fi Web Project Number | BU26PPE73M | ID | Fi Web confirmed
iNFADS RPUID | 51473 | ID | iNFADS Real Property record
Primary Project CCN | 44112 | CCN | iNFADS CCN 44112
Total Building GSF | 30973 | SF | iNFADS confirmed
Plant Replacement Value (iNFADS) | 26636215 | $ | iNFADS confirmed; UFC 3-701-01 w/Ch 7
Estimate Date | 29 Apr 2026 | Date | Date of estimate production
Estimate Level | Level 3 ROM | Text | UFS 3-740-05 (2 Feb 2026); for information only
Delivery Method | Design-Build (DB) | Method | UFC 3-730-01 (2024)
COST INPUTS (yellow = user input; locked unless directed)
Base Year | 2024 | FY | FY24 CONUS base costs
Target Fiscal Year | 2027 | FY | FY27 construction start
Area Cost Factor (ACF) | 1.85 | Multiplier | UFC 3-701-01 w/Ch 7 (25 Jul 2025), Table 4-1 OCONUS Okinawa M67400-0004
Escalation Rate (annual) | 0.021 | % | OSD FY25 published rate, client confirmed
Escalation Years | 3 | Years | FY24 base to FY27 target
General Requirements | 0.1 | % | FSRM program-directed; UFS 3-740-05
PAX ASSOCIATED COSTS (informational; applied by PAX at submission)
Contingency | 10% | % | FSRM program-directed; PAX-applied to items subtotal
Supervision Inspection and Overhead (SIOH) | 8% | % | OCONUS FSRM customer-directed (8.0%); PAX-applied
Design-Build Design (DB) | 4% | % | UFC 3-730-01 (2024); PAX-applied
Planning and Design (P&D) | 6% | % | NON ADD; informational only; does not roll into TPC
DERIVED VALUES (live formulas; do not edit)
Compound Escalation Factor |  | Factor | (1 + escalation)^years
Base Direct Cost (FY24 CONUS) |  | $ | Sum of all scope items on SCOPE_DETAIL
Pre-Calibration Subtotal |  | $ | Base Direct x ACF x Escalation x (1 + General Requirements)
Locked Total Project Cost | 1455526 | $ | PAX-locked TPC; reconciliation target
Items Subtotal Target (PAX paste) |  | $ | Locked TPC / 1.23552 (1.10 x 1.08 x 1.04)
Cost Adjustment Factor |  | Factor | Items Subtotal Target / Pre-Calibration Subtotal; calibrates ROM chain to locked TPC
PLANNING RATES
JPY/USD Planning Rate | 150.4415 | Rate | FY26 budget planning rate; H.10 live rate at PAX submission
ACTIVE REFERENCES
MCO 11000.5 (03 Jun 2016) ¦ Real Property FSRM Program
MCO 11000.12 (08 Sep 2014) ¦ Real Property Facilities Manual
Consistency Review Board Guidelines (May 2024, REV #15) ¦ DD Form 1391 line-item sequencing
UFC 3-701-01 with Change 7 (25 Jul 2025) ¦ PUC, ACF, PRV authority
UFC 3-730-01 (2024) ¦ Design-Build contracting
UFS 3-740-05 (02 Feb 2026) ¦ Cost estimating ROM levels
JED Cost Estimating Guidance (Combined, Nov 2025)
Japan District Design Guide v9 (April 2025)
10 U.S.C. Section 2802 ¦ DoD 4270.5-M ¦ Classification of Work

## DD1391_BLOCK9
SCH-3237 ¦ DD FORM 1391 BLOCK 9 - PAX PASTE ¦ LEVEL 3 ROM ¦ FY27 ¦ PAX ID 387622 ¦ Fi Web BU26PPE73M
All amounts in $000s. Paste discipline rollups into PAX Block 9 items table; PAX-loaded Cont 10% / SIOH 8% / DB 4% render the printed Total Project Cost. P&D 6% NON ADD shown for visibility.
Cost Element | Amount ($000) | Notes / UNIFORMAT
C10 ¦ Interior Construction |  | UNIFORMAT II Lv2 C10 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
D30 ¦ HVAC / Mechanical |  | UNIFORMAT II Lv2 D30 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
D50 ¦ Electrical / Communications |  | UNIFORMAT II Lv2 D50 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
F10 ¦ Hazardous Material Abatement |  | UNIFORMAT II Lv2 F10 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
ITEMS SUBTOTAL (PAX Block 9 paste total) |  | Sum of discipline rollups; this is the value pasted into PAX items table
Contingency (10.0%) PAX-applied |  | 10% of items subtotal; FSRM program-directed
Total Contract Cost |  | Items subtotal x 1.10
SIOH (8.0%) PAX-applied |  | 8% of TCC; OCONUS FSRM customer-directed
Total Funded Cost |  | TCC x 1.08
DB Design (4.0%) PAX-applied |  | 4% of TFC; UFC 3-730-01 (2024)
TOTAL PROJECT COST |  | TFC x 1.04 = items subtotal x 1.23552
TOTAL PROJECT COST ($000 rounded) |  | Printed TPC on DD Form 1391 face
Planning and Design (6.0%) NON ADD |  | Informational; does not roll into TPC; PAX renders separately on form
Reconciliation (must equal 0) |  | Printed TPC ($000) minus Locked TPC ($000)
CLASSIFICATION OF WORK
Construction |  | 100% of Total Project Cost ¦ 10 U.S.C. Section 2802
Special Interest: Restoration and Modernization |  | 100% SRM ¦ MCO 11000.12 ¦ DoD 4270.5-M