## ESTIMATE
SCH-3213 ¦ ROM COST ESTIMATE ¦ LEVEL 3 ¦ FY27 ¦ PAX ID 387624 ¦ Fi Web BU26PPE72M
A. ROM FORMULA CHAIN (live formulas reference PARAMETERS tab)
Step | Element | Amount ($) | Formula / Source
1 | Base Direct Cost (FY24 CONUS) |  | Sum of all scope items on SCOPE_DETAIL
2 | x ACF 1.85 (Camp Schwab Okinawa) |  | UFC 3-701-01 w/Ch 7 (25 Jul 2025), Table 4-1
3 | x Compound Escalation Factor |  | OSD FY25 published rate; FY24 to FY27
4 | x (1 + General Requirements 10%) |  | FSRM program-directed; UFS 3-740-05
5 | x Cost Adjustment Factor (calibrated) |  | Calibrates ROM chain to locked TPC; absorbs base-cost adjustments
| ITEMS SUBTOTAL (PAX Block 9 paste total) |  | Calibrated to PAX rollup chain
B. PAX ROLLUP VERIFICATION (mirrors what PAX prints on the form; DB applied to items, not to TFC)
Step | Element | Amount ($) | Formula / Source
| Items Subtotal |  | From Section A; pasted into PAX Block 9
| + Contingency (10.0%) PAX-applied |  | FSRM program-directed
| Total Contract Cost (TCC) |  | ROUND(items subtotal x 1.10)
| + SIOH (8.0%) PAX-applied |  | OCONUS FSRM customer-directed; ROUND(TCC x 0.08)
| Total Funded Cost (TFC) |  | ROUND(TCC x 1.08)
| + DB Design (4.0%) PAX-applied |  | UFC 3-730-01 (2024); PAX applies DB to items, not to TFC
| TOTAL PROJECT COST |  | TFC + DB Design (mirrors PAX Total Request)
| TOTAL PROJECT COST ($000 rounded) |  | Printed face value on DD Form 1391
| Locked TPC ($000 rounded) |  | Reconciliation target
| Reconciliation (must equal 0) |  | Printed minus Locked
| Planning and Design (6.0%) NON ADD |  | Informational; does not roll into TPC
C. UNIFORMAT II LV2 SUMMARY (Base Direct pre-ACF, by category)
Code | Category | Base Direct ($) | Description
B20 | Exterior Enclosure |  | 2 scope item(s)
C10 | Interior Construction |  | 32 scope item(s)
D20 | Plumbing |  | 9 scope item(s)
D30 | HVAC / Mechanical |  | 14 scope item(s)
D50 | Electrical / Communications |  | 11 scope item(s)
F10 | Hazardous Material Abatement |  | 5 scope item(s)
TOTAL BASE DIRECT (must equal Section A row 5)
D. METHODOLOGY
Estimate Level | Level 3 ROM per UFS 3-740-05 (02 Feb 2026). Non-mandatory supplement; for information only.
Scope Basis | 73 discrete work items across 6 UNIFORMAT II Lv2 categories. Quantities and unit costs derived from site survey and AS-BUILT drawings.
Area Cost Factor | 1.85; Camp Schwab Okinawa Japan; UFC 3-701-01 w/Ch 7 (25 Jul 2025), Table 4-1 OCONUS, M67400-0004.
Escalation | 2.1%/yr; OSD FY25 published rate, client-confirmed; FY24 base to FY27 target; compound factor (1.021)^3 = 1.0643.
General Requirements | 10.0%; FSRM program-directed; UFS 3-740-05.
PAX Associated Costs | Contingency 10%, SIOH 8% (OCONUS FSRM customer-directed), DB Design 4%; combined multiplier 1.23552. Planning and Design 6% NON ADD; informational only.
Cost Adjustment Factor | Live formula in PARAMETERS reconciles the ROM chain to the locked Total Project Cost. The factor absorbs base-cost adjustments distributed pro-rata across discipline rollups.
Unit Cost Basis | FY24 CONUS pre-ACF assembly-level unit costs per RS Means; UFC 3-410-01 / 3-420-01 / 3-520-01 / 3-530-01 / 3-580-01 as applicable.
Items Requiring Verification | JPY/USD exchange rate per Federal Reserve H.10 on date of PAX submission.
Prepared By | Anthony L. Potter ¦ Facilities Planner ¦ MCIPAC G-F PPE ¦ 29 Apr 2026
E. VERSION HISTORY
Version | Date | Total Project Cost ($) | Notes
Current | 29 Apr 2026 |  | 4-tab discipline-rollup architecture; PAX-pasteable Block 9; reconciles to locked TPC

## SCOPE_DETAIL
SCH-3213 ¦ SCOPE DETAIL & QUANTITY TAKEOFF ¦ BASE YEAR FY24 CONUS DIRECT COSTS ¦ Fi Web BU26PPE72M
Yellow = confirmed scope. White = formula-driven extended cost. All unit costs are FY24 CONUS pre-ACF, assembly-level RS Means basis.
Item | Group | Work Description | Qty | Unit | Unit Cost (FY24 CONUS) | Extended Cost | UNIFORMAT II Lv2 | Cost Basis / Notes
1. TELECOM INFRASTRUCTURE MODERNIZATION
1 | Telecom | Demo existing telecom equipment, racks, cabling, and legacy infrastructure in telecom room | 1 | LS | 12000 |  | D50 | RS Means FY24 CONUS: Equipment and cable demolition, telecom room. RSM 28 05 05.
2 | Telecom | Construct new telecom room - equipment racks, UPS, patch panels, grounding bus bar, EPO, fire suppression, HVAC, raised floor | 1 | LS | 65000 |  | D50 | RS Means FY24 CONUS: Telecom room build-out, commercial, complete. RSM 28 05 13.
3 | Telecom | Install OSP fiber optic cable from base telecom demarcation point to building telecom room | 1 | LS | 15000 |  | D50 | RS Means FY24 CONUS: OSP fiber, includes conduit, pull boxes, termination. RSM 27 13 23.
4 | Telecom | Install ISP horizontal cabling - Cat6A to all converted office and work spaces (30 drops) | 30 | EA | 1200 |  | D50 | RS Means FY24 CONUS: Cat6A horizontal cable, pull, terminate, test, 90 LF avg run. RSM 27 15 43.
5 | Telecom | Install new work area outlets (WAOs) - quad WAO in all converted office spaces (24 EA) | 24 | EA | 1000 |  | D50 | RS Means FY24 CONUS: Quad data outlet, flush mounted, complete. RSM 27 15 43.
6 | Telecom | Building grounding system verification and upgrade for telecom modernization per TIA-607-C | 1 | LS | 8000 |  | D50 | RS Means FY24 CONUS: Telecom grounding, commercial building, per TIA-607-C. RSM 26 05 26.
2. S-2 VAULT CONSTRUCTION - TWO VAULT SPACES
7 | S-2 Vault | New reinforced vault walls with structural supports - CMU or CIP concrete, 2 EA (one per vault space) | 2 | EA | 28000 |  | C10 | RS Means FY24 CONUS: CMU reinforced vault wall, 8-in block, grouted solid. RSM 04 22 00.
8 | S-2 Vault | GSA Class V vault door, frame, flange set, hardware, certified installation, prorated air freight - 2 EA per MCO 5530.14A + UFC 4-010-05 | 2 | EA | 14599 |  | C10 | Direct procurement: Hamilton CI-5 Class V vault door, TQL Global shipment, all-in unit cost confirmed.
9 | S-2 Vault | IDS sensor installation - 2 vault spaces: PIR, magnetic door contact, keypad per vault, ESAMS compliant | 2 | EA | 8000 |  | C10 | RS Means FY24 CONUS: IDS zone sensor package, vault, 2-zone config. RSM 28 16 16.
10 | S-2 Vault | Vault electrical - LED lighting, outlets, emergency egress lighting per vault space, 2 EA | 2 | EA | 6000 |  | C10 | RS Means FY24 CONUS: Vault electrical package, lighting and power, per space. RSM 26 05 19.
11 | S-2 Vault | Dedicated vault ventilation - supply/exhaust isolation with damper per GSA Class V vault requirements, 2 EA | 2 | EA | 12000 |  | C10 | RS Means FY24 CONUS: Vault HVAC isolation, supply/exhaust with fire/smoke damper, per vault. RSM 23 33 00.
12 | S-2 Vault | Vault interior finishes - VCT flooring, interior paint, base molding, 2 EA (one per vault space) | 2 | EA | 3000 |  | C10 | RS Means FY24 CONUS: VCT flooring and interior paint, per room, commercial. RSM 09 65 13.
3. SIPR NETWORK RACK INSTALLATION
13 | SIPR | Lockable wall-mount SIPR enclosure/rack with backboard and grounding bus bar - CNSSAM TEMPEST/01-13 compliant | 1 | LS | 25000 |  | D50 | RS Means FY24 CONUS: SIPR-capable wall rack enclosure, lockable, with grounding, TEMPEST compliant. RSM 27 11 13.
14 | SIPR | Fiber optic cable from telecom room to SIPR rack location - single-mode, conduit, termination | 1 | LS | 8000 |  | D50 | RS Means FY24 CONUS: Single-mode fiber in conduit, terminate both ends. RSM 27 13 23.
15 | SIPR | SIPR-capable work area outlets (WAOs) - 6 EA at SIPR workstations | 6 | EA | 1000 |  | D50 | RS Means FY24 CONUS: Data outlet, quad, flush mounted, complete. RSM 27 15 43.
16 | SIPR | Conduit and cable management infrastructure for SIPR runs - dedicated conduit, cable tray, hardware | 1 | LS | 6000 |  | D50 | RS Means FY24 CONUS: Conduit and cable tray, SIPR zone separation, complete. RSM 26 05 33.
4. PATHWAY - BN CONFERENCE ROOM TO S-2 VAULT
17 | Pathway | New door opening in existing wall - saw cut, structural header, threshold plate for vault access pathway | 1 | EA | 5000 |  | C10 | RS Means FY24 CONUS: Saw cut opening in CMU/concrete wall, structural header, complete. RSM 03 30 00.
18 | Pathway | New security-rated door/frame/hardware for vault access pathway between Bn Conference Room and S-2 vault | 1 | EA | 3500 |  | C10 | RS Means FY24 CONUS: HM door 3x7, frame, lever hardware, complete. RSM 08 11 13.
19 | Pathway | New partition walls to define pathway corridor between Bn Conference Room and S-2 vault | 1 | LS | 8000 |  | C10 | RS Means FY24 CONUS: GWB stud partition, 3-5/8-in metal stud, 10-ft height, complete. RSM 09 29 00.
20 | Pathway | Pathway finishes - VCT flooring, interior paint, base molding | 1 | LS | 2500 |  | C10 | RS Means FY24 CONUS: VCT and interior paint, corridor, commercial grade. RSM 09 65 13.
21 | Pathway | Fire alarm devices in new pathway/corridor - smoke detector and horn/strobe notification device per NFPA 72 | 1 | LS | 2200 |  | C10 | RS Means FY24 CONUS: Smoke detector and notification appliance, addressable, complete. RSM 28 31 11.
22 | Pathway | Exit sign addition/relocation for new egress path through corridor per NFPA 101 / IBC Chapter 10 | 1 | EA | 500 |  | C10 | RS Means FY24 CONUS: LED exit sign, wall/ceiling mount, complete. RSM 26 53 13.
5. CONSTRUCT 6 PRIVATE OFFICES
23 | Offices | New gypsum stud partition walls for 6 private offices - built over existing work bench infrastructure per client direction | 6 | EA | 10000 |  | C10 | RS Means FY24 CONUS: GWB partition, 3-5/8-in stud, 10-ft height, per office bay. RSM 09 29 00.
24 | Offices | New door/frame/hardware per office - 6 EA | 6 | EA | 2500 |  | C10 | RS Means FY24 CONUS: HM door 3x7, frame, lever hardware, complete. RSM 08 11 13.
25 | Offices | Electrical - outlets, switches, and LED lighting per office, 6 EA | 6 | EA | 3000 |  | C10 | RS Means FY24 CONUS: Branch circuit, 4 outlets + 2 switches + 2 LED fixtures per office. RSM 26 05 19.
26 | Offices | Emergency egress lighting per office - 6 EA per NFPA 101 / UFC 3-530-01 | 6 | EA | 600 |  | C10 | RS Means FY24 CONUS: Battery-backed egress light, wall mount, complete. RSM 26 53 16.
27 | Offices | Fire alarm devices in new office spaces - smoke detector and horn/strobe per NFPA 72, 6 EA | 6 | EA | 1800 |  | C10 | RS Means FY24 CONUS: Smoke detector + notification appliance, addressable, per office. RSM 28 31 11.
28 | Offices | VCT flooring per office - 6 EA | 6 | EA | 1500 |  | C10 | RS Means FY24 CONUS: VCT 12x12, commercial grade, including adhesive and base. RSM 09 65 13.
29 | Offices | Interior paint per office - 6 EA | 6 | EA | 800 |  | C10 | RS Means FY24 CONUS: Interior latex paint, 2 coats, walls and ceiling per office. RSM 09 91 13.
30 | Offices | Exit sign addition/relocation for new office cluster egress configuration - 3 EA per NFPA 101 / IBC Ch. 10 | 3 | EA | 500 |  | C10 | RS Means FY24 CONUS: LED exit sign, wall/ceiling mount, complete. RSM 26 53 13.
6. EOD OFFICE PARTITION
31 | EOD Office | New gypsum stud partitions for EOD office space division | 1 | LS | 12000 |  | C10 | RS Means FY24 CONUS: GWB partition, 3-5/8-in stud, 10-ft height, complete. RSM 09 29 00.
32 | EOD Office | New door/frame/hardware for partitioned EOD spaces - 2 EA | 2 | EA | 2500 |  | C10 | RS Means FY24 CONUS: HM door 3x7, frame, lever hardware, complete. RSM 08 11 13.
33 | EOD Office | Electrical modifications for partitioned EOD spaces - outlets, switches, lighting | 1 | LS | 5000 |  | C10 | RS Means FY24 CONUS: Branch circuit extension, 4 outlets + 2 switches + 2 LED fixtures. RSM 26 05 19.
34 | EOD Office | Emergency egress lighting for new EOD partitioned spaces per NFPA 101 / UFC 3-530-01 | 1 | LS | 1200 |  | C10 | RS Means FY24 CONUS: Battery-backed egress light, wall mount, 2 EA. RSM 26 53 16.
35 | EOD Office | Fire alarm devices - smoke detectors and notification devices for new EOD partitioned spaces per NFPA 72 | 1 | LS | 3600 |  | C10 | RS Means FY24 CONUS: Smoke detector + notification appliance, addressable, 2 EA. RSM 28 31 11.
36 | EOD Office | Finishes - VCT flooring and interior paint for EOD partitioned spaces | 1 | LS | 4500 |  | C10 | RS Means FY24 CONUS: VCT and 2-coat interior paint, commercial, LS per space. RSM 09 65 13.
37 | EOD Office | Exit sign relocation for new EOD partition egress configuration per NFPA 101 / IBC Chapter 10 | 1 | EA | 500 |  | C10 | RS Means FY24 CONUS: LED exit sign, wall/ceiling mount, complete. RSM 26 53 13.
7. CONSTRUCT SECURE STORAGE - UNIT MAIL ROOM
38 | Mail Room | New partition walls to establish Unit Mail Distribution Point per MCO 5110.1 / DoD 4525.6-M - programmed approx. 175 SF - CCN 61010 per UFC 3-701-01 - built over existing bench/shelf infrastructure per client direction | 1 | LS | 8000 |  | C10 | RS Means FY24 CONUS: GWB partition, 3-5/8-in stud, 10-ft height, LS for mail room enclosure. RSM 09 29 00.
39 | Mail Room | Security door/frame/lockset/closer for secure mail room | 1 | EA | 6000 |  | C10 | RS Means FY24 CONUS: HM door with security lockset, closer, and reinforced frame. RSM 08 11 13.
40 | Mail Room | Electrical - outlets and LED lighting in secure storage area | 1 | LS | 3500 |  | C10 | RS Means FY24 CONUS: Branch circuit, 2 outlets + 2 LED fixtures, complete. RSM 26 05 19.
41 | Mail Room | Fire alarm device - smoke detector for new enclosed mail room per NFPA 72 | 1 | EA | 1200 |  | C10 | RS Means FY24 CONUS: Addressable smoke detector, complete. RSM 28 31 11.
42 | Mail Room | Finishes - VCT flooring and interior paint in secure mail room | 1 | LS | 2500 |  | C10 | RS Means FY24 CONUS: VCT and 2-coat interior paint, commercial. RSM 09 65 13.
8. HAZARDOUS MATERIALS - SURVEY AND ABATEMENT
43 | HAZMAT | ACM re-inspection and survey confirmation - verify 2001 Bhate Environmental survey findings, full building pre-design per full HVAC duct and plumbing floor demolition scope | 1 | LS | 6000 |  | F10 | Bhate Environmental Associates 2001, NVLAP accredited PLM. Re-inspection required - 25-yr survey age and full system replacement scope per UFC 3-470-06.
44 | HAZMAT | Lead-Based Paint (LBP) survey - whole building pre-design per UFC 3-470-03 and EPA RRP Rule 40 CFR Part 745 | 1 | LS | 4000 |  | F10 | RS Means FY24 CONUS: LBP inspection and risk assessment, commercial building, 13,484 SF. RSM 02 82 16.
45 | HAZMAT | Targeted ACM abatement - H2 rose 12x12 floor tile, 570 SF, Corridor 100/Rooms 8 and 23, 4% Chrysotile non-friable; full plumbing DWV replacement triggers floor demolition per OSHA 1926.1101 | 570 | SF | 32 |  | F10 | Bhate 2001 confirmed: H2, 570 SF, 4% Chrysotile, non-friable, good condition. Abatement triggered by confirmed floor demolition scope. RS Means FY24 CONUS RSM 02 82 13.13.
46 | HAZMAT | HAZMAT contractor mobilization, containment setup, negative air, air monitoring, and post-abatement clearance testing | 1 | LS | 8000 |  | F10 | RS Means FY24 CONUS: HAZMAT contractor mobilization, commercial abatement project, complete. RSM 02 82 13.
47 | HAZMAT | ACM contingency allowance - potential ceiling tile and duct insulation disturbance building-wide per full HVAC duct replacement scope; 13,484 SF per UFC 3-470-06; confirm or remove at design following re-inspection per Item 43 | 13484 | SF | 5 |  | F10 | Level 3 ROM allowance $5/SF per UFC 3-470-06 guidance. Included in hard scope. Confirm or remove at design following re-inspection per Item 43. RS Means FY24 CONUS: ACM ceiling/insulation abatement allowance.
9. HVAC FULL SYSTEM REPLACEMENT
48 | HVAC | Demo existing central chilled water plant - chiller C-1, AHU-1, BC-1 booster coil, pumps P-1 (2 EA), expansion tanks EWT-1/EWT-2, reheat coil RH-1, controls, and associated peripherals per as-built equipment schedule Sheet 5-20 | 1 | LS | 22000 |  | D30 | RS Means FY24 CONUS: Mechanical equipment demolition and disposal, central chilled water plant, 80-100 ton class. RSM 15 21 05.
49 | HVAC | Demo existing ductwork building-wide - all supply, return, and exhaust sheet metal duct, hangers, insulation, diffusers, and registers, 13,484 SF; original 1984 construction past ASHRAE 30-yr service life per mechanical evaluation 19 Mar 2026 | 13484 | SF | 3.5 |  | D30 | RS Means FY24 CONUS: Sheet metal ductwork demolition, existing commercial building, per SF floor area. RSM 23 07 13.
50 | HVAC | Remove fuel oil tank OT-1 (240-gal above-ground steel) and all fuel oil supply and return piping - boiler B-1 system removal | 1 | LS | 8500 |  | D30 | RS Means FY24 CONUS: Above-ground storage tank removal and disposal, 240-gal steel tank, includes transport. RSM 02 82 13.
51 | HVAC | Remove abandoned compressed air system - air compressor, distribution piping, and outlets building-wide | 1 | LS | 5500 |  | D30 | RS Means FY24 CONUS: Compressed air system demolition, piping removal, existing building. RSM 15 21 05.
52 | HVAC | New air-cooled chilling unit, 86 ton (302 kW), pad-mounted exterior - new concrete equipment pad, refrigerant piping, electrical disconnect, startup and commissioning; replaces C-1 per as-built equipment schedule Sheet 5-20 | 1 | EA | 108000 |  | D30 | RS Means FY24 CONUS: Air-cooled chiller, 80-100 ton, complete with refrigerant charge, controls, and commissioning. RSM 23 64 16.
53 | HVAC | New air handling unit, floor-setting horizontal type, approximately 7,000 CFM - filters, coils, fan section, drain pan, and electrical connection; replaces AHU-1 per equipment schedule Sheet 5-20 | 1 | EA | 52000 |  | D30 | RS Means FY24 CONUS: Air handling unit, horizontal, 5,000-8,000 CFM range, complete. RSM 23 74 33.
54 | HVAC | New circulation pumps, centrifugal, 2 EA - pipe flanges, flexible connectors, isolation valves, motor starters, and electrical connections; replaces P-1 x2 per equipment schedule | 2 | EA | 9500 |  | D30 | RS Means FY24 CONUS: Centrifugal pump, base-mounted, 1.5-3 HP, complete with fittings and starters. RSM 23 21 13.
55 | HVAC | New booster coil unit, duct insertion type - electrical connection and duct reconnection; replaces BC-1 per equipment schedule Sheet 5-20 | 1 | EA | 17500 |  | D30 | RS Means FY24 CONUS: Duct insertion electric heating coil unit, commercial, complete. RSM 23 83 16.
56 | HVAC | New chilled water distribution piping, Type L copper, insulated, building-wide - main supply and return runs, branch lines, isolation valves, balance valves, and pressure testing; approximately 350 LF from piping diagram Sheet 10-20 | 1 | LS | 24000 |  | D30 | RS Means FY24 CONUS: Copper pipe, insulated, chilled water distribution, 2-in dia avg, 350 LF estimated. RSM 23 21 13.16.
57 | HVAC | New supply and return ductwork, diffusers, registers, and volume dampers building-wide - sheet metal fab, hangers, insulation, and all air distribution devices for 24 rooms per 1st floor duct plan Sheet 11-20; 13,484 SF | 13484 | SF | 15 |  | D30 | RS Means FY24 CONUS: HVAC ductwork system, supply and return, commercial, complete per SF floor area. RSM 23 31 13.
58 | HVAC | New power roof ventilators - replace RF-1 through RF-6 per as-built equipment schedule Sheet 5-20; 9 EA per field count confirmed | 9 | EA | 5500 |  | D30 | RS Means FY24 CONUS: Power roof ventilator, centrifugal, 1,000-15,000 CFM, complete. RSM 23 34 23.
59 | HVAC | New gravity roof ventilators - replace GV-1 and GF-2, 2 EA per as-built equipment schedule Sheet 5-20 | 2 | EA | 3200 |  | D30 | RS Means FY24 CONUS: Gravity roof ventilator, 300-500 CFM, complete. RSM 23 34 16.
60 | HVAC | New exhaust fans, hanger-mounted centrifugal - replace EF-1, EF-2, EF-3, HF-1, HF-2, 5 EA per as-built equipment schedule Sheet 5-20 | 5 | EA | 2800 |  | D30 | RS Means FY24 CONUS: Centrifugal hanger-mounted exhaust fan, commercial, complete. RSM 23 34 13.
61 | HVAC | DDC/BAS building automation controls - DDC for 24 zones per duct plan Sheet 11-20, central controller, thermostat per zone, wiring, and programming | 1 | LS | 30000 |  | D30 | RS Means FY24 CONUS: DDC HVAC controls, commercial building, 24 zones complete. RSM 25 30 00.
10. PLUMBING FULL REPLACEMENT AND RESTROOM RENOVATION
62 | Plumbing | Demo existing cast iron sanitary DWV piping, floor drains, and cleanouts building-wide; original 1984 construction, 42 years old; per 1st floor piping plan Sheet 8-20 and drain piping isometric Sheet 9-20 | 13484 | SF | 5 |  | D20 | RS Means FY24 CONUS: Cast iron pipe demolition, DWV system, existing commercial building, per SF. RSM 02 41 19.
63 | Plumbing | New Schedule 40 PVC drain, waste, and vent (DWV) system building-wide - all fixture drains, soil stacks, vent stacks, and cleanouts per IPC 2021; from all fixture locations to first sanitary manhole outside building | 13484 | SF | 10.5 |  | D20 | RS Means FY24 CONUS: PVC DWV system, commercial building, complete per SF floor area. RSM 22 11 16.
64 | Plumbing | Demo existing domestic water piping (cold water supply and domestic hot water distribution) building-wide; all branch piping serving restrooms, mech room, hose bibs, and service sink; per piping plan Sheet 8-20 | 13484 | SF | 3.5 |  | D20 | RS Means FY24 CONUS: Domestic water piping demolition, existing commercial building, per SF. RSM 02 41 19.
65 | Plumbing | New Type L copper cold water distribution system building-wide - water service entry through building to all fixture locations, isolation valves, pressure-reducing valves, and hose bibs | 13484 | SF | 9 |  | D20 | RS Means FY24 CONUS: Copper domestic cold water distribution, commercial, per SF floor area. RSM 22 11 13.
66 | Plumbing | New building drain connection to sanitary sewer - remove and replace existing site sewer line, new PVC 6-inch SDR-35 from building exit to first manhole, excavation, backfill, and surface restoration | 1 | LS | 7500 |  | D20 | RS Means FY24 CONUS: PVC SDR-35 site sewer, 6-in dia, 50 LF estimated, includes excavation and backfill. RSM 33 31 13.
67 | Plumbing | New commercial electric water heater, 100-gallon - remove existing 2004 unit past service life, install new unit with supply connections, T&P relief valve, floor drain piping, and electrical connection | 1 | EA | 5200 |  | D20 | RS Means FY24 CONUS: Commercial electric water heater, 80-100 gal, furnished and installed complete. RSM 22 33 30.
68 | Plumbing | Full restroom fixture replacement, all restroom spaces (Rooms 108A, 108B, 110A, 110B) - water closets 4 EA, urinals 3 EA, lavatories 3 EA, shower sets 2 EA, service sink 1 EA; per plumbing fixture schedule Sheet 7-20 | 1 | LS | 16500 |  | D20 | RS Means FY24 CONUS: Fixture replacement package per schedule Sheet 7-20. WC $1,250 EA, urinal $1,000 EA, lavatory $900 EA, shower $1,900 EA, service sink $1,100 EA. RSM 22 41 13.
69 | Plumbing | Restroom ceramic tile, floor and wall, all restroom spaces - floor tile 500 SF and wall tile 1,000 SF (wet areas to 8 ft) per interior finish schedule Sheet 6-20 of as-built drawings | 1 | LS | 25000 |  | D20 | RS Means FY24 CONUS: Ceramic tile floor $18/SF (500 SF = $9,000) and wall $16/SF (1,000 SF = $16,000). RSM 09 30 13.
70 | Plumbing | Restroom accessories replacement - toilet paper holders, towel dispensers, mirrors, soap dispensers, and grab bars, all restroom spaces | 1 | LS | 5200 |  | D20 | RS Means FY24 CONUS: Restroom accessories, commercial grade, 6 spaces x $867 avg. RSM 10 28 16.
71 | Plumbing | Restroom LED lighting replacement - all restroom spaces, 15 fixtures, including conduit, wiring, switches, and circuit connections | 15 | EA | 435 |  | D50 | RS Means FY24 CONUS: LED recessed fixture with box, commercial, complete with wiring. RSM 26 51 00.
11. OVERHEAD DOORS AND AIR CURTAINS
72 | Doors | Replace overhead sectional steel roll-up doors building-wide - remove and replace existing doors past service life per David Brennan mechanical evaluation 19 Mar 2026; 5 EA per as-built floor plan Sheet 7-36 (Rooms 112, 114, 116, 117, 118 north face) | 5 | EA | 5500 |  | B20 | RS Means FY24 CONUS: Overhead sectional steel door, commercial, 10x10 opening, complete with hardware and motor operator. RSM 08 33 23.
73 | Doors | Replace air curtains at building entry doors - remove and replace non-functioning air curtains per David Brennan mechanical evaluation 19 Mar 2026; 2 EA (end of each hallway, confirmed) | 2 | EA | 2900 |  | B20 | RS Means FY24 CONUS: Commercial air curtain, 36-in width, heated, complete with electrical connection. RSM 23 34 43.
TOTAL BASE DIRECT COST (FY24 CONUS)

## PARAMETERS
SCH-3213 ¦ COST ESTIMATE PARAMETERS ¦ LEVEL 3 ROM ¦ FY27 ¦ PAX ID 387624 ¦ Fi Web BU26PPE72M
PROJECT IDENTIFICATION
Estimate Title | SCH-3213 ¦ Repair COMPANY HQ | Text | DD Form 1391 ¦ PAX ID 387624 ¦ Fi Web BU26PPE72M
Building / Installation | SCH-3213 ¦ Camp Schwab, Okinawa, Japan | Text | MCIPAC G-F PPE
Supported Units | 4th Marine Regiment / III MEF | Text | Primary supported units
PAX ID | 387624 | ID | PAX System
Fi Web Project Number | BU26PPE72M | ID | Fi Web confirmed
iNFADS RPUID | 48879 | ID | iNFADS Real Property record
Primary Project CCN | 61010 | CCN | iNFADS CCN 61010
Total Building GSF | 13484 | SF | iNFADS confirmed
Plant Replacement Value (iNFADS) | 10893334 | $ | iNFADS confirmed; UFC 3-701-01 w/Ch 7
Estimate Date | 29 Apr 2026 | Date | Date of estimate production
Estimate Level | Level 3 ROM | Text | UFS 3-740-05 (2 Feb 2026); for information only
Delivery Method | Design-Build (DB) | Method | UFC 3-730-01 (2024)
COST INPUTS (yellow = user input; locked unless directed)
Base Year | 2024 | FY | FY24 CONUS base costs
Target Fiscal Year | 2027 | FY | FY27 construction start
Area Cost Factor (ACF) | 1.85 | Multiplier | UFC 3-701-01 w/Ch 7 (25 Jul 2025), Table 4-1 OCONUS Okinawa M67400-0004
Escalation Rate (annual) | 0.021 | % | OSD FY25 published rate, client confirmed
Escalation Years | 3 | Years | FY24 base to FY27 target
General Requirements | 0.1 | % | FSRM program-directed; UFS 3-740-05
PAX ASSOCIATED COSTS (informational; applied by PAX at submission)
Contingency | 10% | % | FSRM program-directed; PAX-applied to items subtotal
Supervision Inspection and Overhead (SIOH) | 8% | % | OCONUS FSRM customer-directed (8.0%); PAX-applied
Design-Build Design (DB) | 4% | % | UFC 3-730-01 (2024); PAX-applied
Planning and Design (P&D) | 6% | % | NON ADD; informational only; does not roll into TPC
DERIVED VALUES (live formulas; do not edit)
Compound Escalation Factor |  | Factor | (1 + escalation)^years
Base Direct Cost (FY24 CONUS) |  | $ | Sum of all scope items on SCOPE_DETAIL
Pre-Calibration Subtotal |  | $ | Base Direct x ACF x Escalation x (1 + General Requirements)
Locked Total Project Cost | 5397928 | $ | PAX-locked TPC; reconciliation target
Items Subtotal Target ($000) | 4395 | $000 | Calibrated so PAX rollup chain (TPC = TFC + DB-on-items) produces Locked TPC
Items Subtotal Target ($) |  | $ | Items Subtotal Target ($000) x 1000
Cost Adjustment Factor |  | Factor | Items Subtotal Target / Pre-Calibration Subtotal; calibrates ROM chain
PLANNING RATES
JPY/USD Planning Rate | 150.4415 | Rate | FY26 budget planning rate; H.10 live rate at PAX submission
ACTIVE REFERENCES
MCO 11000.5 (03 Jun 2016) ¦ Real Property FSRM Program
MCO 11000.12 (08 Sep 2014) ¦ Real Property Facilities Manual
Consistency Review Board Guidelines (May 2024, REV #15) ¦ DD Form 1391 line-item sequencing
UFC 3-701-01 with Change 7 (25 Jul 2025) ¦ PUC, ACF, PRV authority
UFC 3-730-01 (2024) ¦ Design-Build contracting
UFS 3-740-05 (02 Feb 2026) ¦ Cost estimating ROM levels
JED Cost Estimating Guidance (Combined, Nov 2025)
Japan District Design Guide v9 (April 2025)
10 U.S.C. Section 2802 ¦ DoD 4270.5-M ¦ Classification of Work

## DD1391_BLOCK9
SCH-3213 ¦ DD FORM 1391 BLOCK 9 - PAX PASTE ¦ LEVEL 3 ROM ¦ FY27 ¦ PAX ID 387624 ¦ Fi Web BU26PPE72M
All amounts in $000s. Paste discipline rollups into PAX Block 9 items table; PAX-loaded Cont 10% / SIOH 8% / DB 4% render the printed Total Project Cost. P&D 6% NON ADD shown for visibility.
Cost Element | Amount ($000) | Notes / UNIFORMAT
B20 ¦ Exterior Enclosure |  | UNIFORMAT II Lv2 B20 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
C10 ¦ Interior Construction |  | UNIFORMAT II Lv2 C10 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
D20 ¦ Plumbing |  | UNIFORMAT II Lv2 D20 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
D50 ¦ Electrical / Communications |  | UNIFORMAT II Lv2 D50 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
F10 ¦ Hazardous Material Abatement |  | UNIFORMAT II Lv2 F10 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
D30 ¦ HVAC / Mechanical |  | UNIFORMAT II Lv2 D30 rollup; balanced to Items Subtotal Target (absorbs rounding from other rollups)
ITEMS SUBTOTAL (PAX Block 9 paste total) |  | Sum of discipline rollups; this is the value pasted into PAX items table
Contingency (10.0%) PAX-applied |  | 10% of items subtotal; FSRM program-directed
Total Contract Cost (TCC) |  | ROUND(items subtotal x 1.10)
SIOH (8.0%) PAX-applied |  | 8% of TCC; OCONUS FSRM customer-directed
Total Funded Cost (TFC) |  | ROUND(TCC x 1.08)
DB Design (4.0%) PAX-applied |  | ROUND(items subtotal x 0.04); PAX applies DB to items, not to TFC
TOTAL PROJECT COST |  | TFC + DB Design (mirrors PAX Total Request)
TOTAL PROJECT COST ($000 rounded) |  | Printed TPC on DD Form 1391 face
Planning and Design (6.0%) NON ADD |  | Informational; does not roll into TPC; PAX renders separately on form
Reconciliation (must equal 0) |  | Printed TPC ($000) minus Locked TPC ($000)
CLASSIFICATION OF WORK
Construction |  | 100% of Total Project Cost ¦ 10 U.S.C. Section 2802
Special Interest: Restoration and Modernization |  | 100% SRM ¦ MCO 11000.12 ¦ DoD 4270.5-M