## ESTIMATE
SCH-1024 ¦ ROM COST ESTIMATE ¦ LEVEL 3 ¦ FY27 ¦ PAX ID 387356 ¦ Fi Web BU26PPE70M
A. ROM FORMULA CHAIN (live formulas reference PARAMETERS tab)
Step | Element | Amount ($) | Formula / Source
1 | Base Direct Cost (FY24 CONUS) |  | Sum of all scope items on SCOPE_DETAIL
2 | x ACF 1.85 (Camp Schwab Okinawa) |  | UFC 3-701-01 w/Ch 7 (25 Jul 2025), Table 4-1
3 | x Compound Escalation Factor |  | OSD FY25 published rate; FY24 to FY27
4 | x (1 + General Requirements 10%) |  | FSRM program-directed; UFS 3-740-05
5 | x Cost Adjustment Factor (calibrated) |  | Calibrates ROM chain to locked TPC; absorbs base-cost adjustments
| ITEMS SUBTOTAL (PAX Block 9 paste total) |  | Equals Locked TPC / 1.23552
B. PAX ROLLUP VERIFICATION (mirrors what PAX prints on the form)
Step | Element | Amount ($) | Formula / Source
| Items Subtotal |  | From Section A
| + Contingency (10.0%) PAX-applied |  | FSRM program-directed
| Total Contract Cost |  | Items Subtotal x 1.10
| + SIOH (8.0%) PAX-applied |  | OCONUS FSRM customer-directed
| Total Funded Cost |  | Total Contract Cost x 1.08
| + DB Design (4.0%) PAX-applied |  | UFC 3-730-01 (2024)
| TOTAL PROJECT COST |  | Total Funded Cost x 1.04
| TOTAL PROJECT COST ($000 rounded) |  | Printed face value on DD Form 1391
| Locked TPC ($000 rounded) |  | Reconciliation target
| Reconciliation (must equal 0) |  | Printed minus Locked
| Planning and Design (6.0%) NON ADD |  | Informational; does not roll into TPC
C. UNIFORMAT II LV2 SUMMARY (Base Direct pre-ACF, by category)
Code | Category | Base Direct ($) | Description
B20 | Exterior Enclosure |  | 2 scope item(s)
C10 | Interior Construction |  | 7 scope item(s)
C30 | Interior Finishes |  | 8 scope item(s)
D20 | Plumbing |  | 6 scope item(s)
D30 | HVAC / Mechanical |  | 8 scope item(s)
D40 | Fire Protection |  | 1 scope item(s)
D50 | Electrical / Communications |  | 11 scope item(s)
E20 | Furnishings |  | 1 scope item(s)
F20 | Selective Demolition |  | 18 scope item(s)
G10 | Site Preparation |  | 1 scope item(s)
G20 | Site Improvements |  | 6 scope item(s)
TOTAL BASE DIRECT (must equal Section A row 5)
D. METHODOLOGY
Estimate Level | Level 3 ROM per UFS 3-740-05 (02 Feb 2026). Non-mandatory supplement; for information only.
Scope Basis | 69 discrete work items across 11 UNIFORMAT II Lv2 categories. Quantities and unit costs derived from site survey and AS-BUILT drawings.
Area Cost Factor | 1.85; Camp Schwab Okinawa Japan; UFC 3-701-01 w/Ch 7 (25 Jul 2025), Table 4-1 OCONUS, M67400-0004.
Escalation | 2.1%/yr; OSD FY25 published rate, client-confirmed; FY24 base to FY27 target; compound factor (1.021)^3 = 1.0643.
General Requirements | 10.0%; FSRM program-directed; UFS 3-740-05.
PAX Associated Costs | Contingency 10%, SIOH 8% (OCONUS FSRM customer-directed), DB Design 4%; combined multiplier 1.23552. Planning and Design 6% NON ADD; informational only.
Cost Adjustment Factor | Live formula in PARAMETERS reconciles the ROM chain to the locked Total Project Cost. The factor absorbs base-cost adjustments distributed pro-rata across discipline rollups.
Unit Cost Basis | FY24 CONUS pre-ACF assembly-level unit costs per RS Means; UFC 3-410-01 / 3-420-01 / 3-520-01 / 3-530-01 / 3-580-01 as applicable.
Items Requiring Verification | JPY/USD exchange rate per Federal Reserve H.10 on date of PAX submission.
Prepared By | Anthony L. Potter ¦ Facilities Planner ¦ MCIPAC G-F PPE ¦ 29 Apr 2026
E. VERSION HISTORY
Version | Date | Total Project Cost ($) | Notes
Current | 29 Apr 2026 |  | 4-tab discipline-rollup architecture; PAX-pasteable Block 9; reconciles to locked TPC

## SCOPE_DETAIL
SCH-1024 ¦ SCOPE DETAIL & QUANTITY TAKEOFF ¦ BASE YEAR FY24 CONUS DIRECT COSTS ¦ Fi Web BU26PPE70M
Yellow = confirmed scope. White = formula-driven extended cost. All unit costs are FY24 CONUS pre-ACF, assembly-level RS Means basis.
Item | Group | Work Description | Qty | Unit | Unit Cost (FY24 CONUS) | Extended Cost | UNIFORMAT II Lv2 | Cost Basis / Notes
1. ARMORY VAULT CONVERSION - 28 Barracks Rooms to 14 Armory Vaults
4 | Armory | New vault doors/frames/locksets - GSA Class V, Hamilton CI-5 (4 armory hallway locations) | 4 | EA | 14599.4 |  | C10 | Hamilton CI-5 door + flange set: $10,143.40 ¦ Prorated air freight (TQL Global, 5-door shipment CVG-OKA): $1,956.00 ¦ Install labor (certified 2-person crew, OCONUS): $2,500.00 ¦ Unit total: $14,599.40
8 | Armory | Structural walls to support vault doors, drop ceiling infrastructure | 4 | EA | 15000 |  | C10 | Reinforced masonry/concrete walls, headers, lintels for vault door support
5 | Armory | Remove 28 windows/frames and 2 exit doors/frames (30 openings total) | 30 | EA | 500 |  | F20 | Window and door removal incl frame, disposal
6 | Armory | CMU wall enclosures at 17 former window openings | 17 | EA | 5000 |  | B20 | CMU infill 5'x6' openings: block, mortar, rebar, tie-in to existing structure
6 | Armory | New weapons port issue windows - custom steel frame, ballistic rated (11 EA) | 11 | EA | 3500 |  | B20 | Custom fabricated steel-frame weapon issue port windows, installed
7 | Armory | Remove drop ceilings in all 28 armory rooms (6,270 SF) | 6270 | SF | 4 |  | F20 | Ceiling grid/tile removal, disposal
7 | Armory | Paint all armory interior walls - 28 rooms (6,270 SF) | 6270 | SF | 4 |  | C30 | Interior latex paint, wall prep
11 | Armory | Armory bathrooms: Remove CT floor/walls, refinish, paint - 11 bathrooms (~1,650 SF) | 1650 | SF | 10 |  | C30 | Ceramic tile removal, skim coat, paint, VCT. 11 baths x 150 SF
5 | Armory | Remove 11 bathroom fixture sets (toilet, tub, sink, accessories) | 11 | EA | 2500 |  | F20 | Full fixture removal, disconnect, disposal per set
12 | Armory | Cap plumbing lines - 11 armory bathrooms | 11 | EA | 2000 |  | D20 | Cap water supply/drainage, includes access and patching
13 | Armory | Adjust valves to limit deadlegs in capped armory plumbing lines | 1 | LS | 10000 |  | D20 | System-wide valve adjustment to prevent stagnation
10 | Armory | Realign all electrical/mechanical ceiling fixtures after ceiling removal - 28 rooms | 28 | EA | 2000 |  | D30 | Relocate/adjust HVAC diffusers, sprinklers, fire alarm, lighting per room
9 | Armory | Electronic Security System (IDS) - 2 zones, 14 vaults: panel, BMS, PIR, keypads, fiber, conduit | 1 | LS | 400000 |  | D50 | ESAMS-compliant IDS: 2 zones, 14 vault areas, BMS, PIR, keypads, fiber backbone, conduit, testing
14 | Armory | Install 28 new quad Work Area Outlets (WAOs) in armory spaces | 28 | EA | 1000 |  | D50 | Quad WAO: 4-port data/voice outlet, conduit, cabling, termination
15 | Armory | New metal shelves at 11 weapons issue port windows | 11 | EA | 600 |  | E20 | Stainless/galvanized steel shelf, brackets, fasteners
2. ARMORY EXTERIOR - Walkways, Landings, Concrete Pads
2 | Armory Ext | Extend backside walkways - concrete sidewalk, safety railings (~200 LF) | 200 | LF | 200 |  | G20 | Concrete sidewalk, railings, grading, landscaping
3 | Armory Ext | New exterior landing/walkway at 11 weapons issue port windows | 11 | EA | 1400 |  | G20 | Concrete landing pad ~100 SF each at 11 issue window locations
16 | Armory Ext | New exterior concrete pads at issue windows - civil (11 locations x 80 SF) | 880 | SF | 14 |  | G20 | Formed concrete pad, 4 inch, gravel base
3. GYM TO WORKSPACE CONVERSION - CLB-4 Commo Swing Space to 4th MarRegt Admin/Ops
1 | Gym/Admin | Gym hallway: Patch concrete baseboard/wall, paint interior, new VCT flooring | 1 | LS | 5000 |  | C30 | Minor patching, paint, and flooring in gym hallway
4. COMM ROOM & WEAPONS CLEANING AREA
17 | Comm Room | Add exhaust ventilation to new indoor weapons cleaning area | 1 | LS | 15000 |  | D30 | Exhaust fan, ductwork, exterior louver, controls for weapons cleaning fumes
18 | Comm Room | Rec Room: New COMM room 8'x10' w/ gypsum walls, VCT, paint; replace acoustical ceiling | 1 | LS | 15000 |  | C10 | New 80 SF room: partitions, door, ceiling, flooring, paint
20 | Comm Room | Rec Room: New electrical outlets and switches in COMM room | 1 | LS | 8000 |  | D50 | Outlets, switches, dedicated circuits for comm equipment
21 | Comm Room | Split A/C systems for telecom room and COMMSEC storage vault (2 EA) | 2 | EA | 12000 |  | D30 | Ductless mini-split A/C, dedicated cooling for telecom/COMMSEC spaces
5. ADMIN - Laundry Room Conversion to Administrative Workspace
22 | Admin | Adjust HVAC supply duct/diffusers and exhaust for admin use in laundry room | 1 | LS | 8000 |  | D30 | Reroute/adjust ductwork, diffusers, registers for office occupancy
23 | Admin | Cap water supply, drainage, floor drains for washers and utility sink; adjust valves | 1 | LS | 5000 |  | D20 | Cap and seal all laundry plumbing, reduce deadlegs
24 | Admin | Laundry Room: Repaint all interior walls, new VCT flooring (~300 SF) | 300 | SF | 9 |  | C30 | Interior paint + VCT: $4/SF paint + $5/SF VCT
25 | Admin | Remove dryer exhaust duct and cap wall vent | 1 | LS | 1500 |  | F20 | Duct removal, vent cap, patch and paint exterior/interior wall
6. BATHS TO OSS VAULT - Locker Rooms / Sauna / Steam Room to OSS w/ SIPR Network
26 | Baths>OSS | Demo CIP concrete walls in shower/locker/sauna areas for open floorplan | 1 | LS | 30000 |  | F20 | Structural demolition of CIP concrete walls - engineering assessment required for load-bearing
35 | Baths>OSS | Cut CIP wall for new door opening from showers to hallway | 1 | EA | 5000 |  | F20 | Saw-cut CIP wall, install new header/frame - structural engineering required
39 | Baths>OSS | Mens: Complete demo - toilet partitions, CT floor/walls, fixtures, lockers, ceiling, showers | 1 | LS | 14000 |  | F20 | Full gut: 2 toilets, 2 urinals, 2 sinks, 2 showers, partitions, lockers, tile, ceiling
40 | Baths>OSS | Womens: Complete demo - benches, showers, fixtures, CT floor/walls, partitions, ceiling | 1 | LS | 12000 |  | F20 | Full gut: 2 showers, 2 toilets, 2 sinks, partitions, tile, ceiling
30 | Baths>OSS | Sauna Room: Remove all wood seats/benches/ceiling/walls/flooring, brick enclosure, exhaust vents | 1 | LS | 8000 |  | F20 | Complete sauna strip-out to bare structure
43 | Baths>OSS | Steam Room: Remove ceramic tile walls, benches, flooring, door/frame | 1 | LS | 6000 |  | F20 | Complete steam room strip-out including tile and moisture barriers
27 | Baths>OSS | Mens: New ceiling, wall refinish/paint, level floor, VCT, plug drains (~398 SF) | 398 | SF | 35 |  | C30 | Full renovation finishes: ceiling grid/tile, wall prep/paint, floor leveling, VCT
28 | Baths>OSS | Womens: New lighting, VCT flooring, wall refinish/paint, new alum door/frame/lockset (~300 SF) | 300 | SF | 32 |  | C30 | Full renovation finishes + new aluminum entry door assembly
41 | Baths>OSS | Sauna Room: New VCT flooring, refinish concrete walls, new ceiling, entry door (~97 SF) | 97 | SF | 28 |  | C30 | Convert to admin space: floor, walls, ceiling, door
42 | Baths>OSS | Steam Room: New VCT flooring, refinish concrete walls, new ceiling, entry door (~124 SF) | 124 | SF | 28 |  | C30 | Convert to admin space: floor, walls, ceiling, door
31 | Baths>OSS | Fitness Room Vault: New security door/frame/lockset/closure (X-10 combination lock) | 1 | EA | 4000 |  | C10 | Heavy-duty security door with X-10 lock for COMMSEC storage
36 | Baths>OSS | Modify/cap/remove all plumbing - sauna, steam, mens/womens locker rooms | 1 | LS | 18000 |  | D20 | Full plumbing removal/capping across 4 wet areas
37 | Baths>OSS | Install new DX multi-zone split A/C system for new OSS area | 1 | LS | 65000 |  | D30 | Multi-zone VRF/DX: outdoor unit, indoor units, refrigerant piping, controls, startup
29 | Baths>OSS | Steam Room area: New electrical light fixtures, outlets, switches, COMM drops | 1 | LS | 5000 |  | D50 | Electrical fit-out for converted admin space
32 | Baths>OSS | Sauna Room: Remove existing electrical, new lights/outlets/switches, COMM drops | 1 | LS | 7000 |  | D50 | Full electrical replacement for converted space
33 | Baths>OSS | Mens: New electrical light fixtures, outlets, switches, COMM requirements | 1 | LS | 6000 |  | D50 | Electrical fit-out for converted admin space
34 | Baths>OSS | Womens: New electrical fixtures, wiring, outlets, switches, relocate fire alarm | 1 | LS | 6000 |  | D50 | Electrical fit-out + fire alarm relocation
44 | Baths>OSS | Steam Room: Remove electrical fixtures/lights/alarms/wiring | 1 | LS | 3500 |  | F20 | Demo tier electrical removal (supplement item 29)
45 | Baths>OSS | Mens: Remove all electrical light fixtures and switches | 1 | LS | 2000 |  | F20 | Demo tier electrical removal
46 | Baths>OSS | Womens: Remove all electrical fixtures, wiring, outlets, switches | 1 | LS | 2000 |  | F20 | Demo tier electrical removal
38 | Baths>OSS | SIPR network: Lockable wallmount enclosure, backboard, ground bus bar, fiber optic from TR, ~10 quad WAOs, conduit - CNSSAM TEMPEST/01-13 | 1 | LS | 220000 |  | D50 | Full SIPR infrastructure per CNSSAM TEMPEST/01-13: enclosure, backboard, bus bar, fiber, WAOs, conduit, testing
63 | Baths>OSS | OSS Vault entrance: GSA Class V vault door, frame, flange set, hardware, certified installation, and prorated air shipping (1 EA) | 1 | EA | 14599.4 |  | C10 | Hamilton CI-5 door + flange set: $10,143.40 ¦ Prorated air freight (TQL Global, 5-door shipment, CVG-OKA): $1,956.00 ¦ Install labor (certified 2-person crew, OCONUS): $2,500.00 ¦ Unit total: $14,599.40
64 | Baths>OSS | OSS Vault entrance: Structural reinforcement at CIP wall opening for vault door emplacement (steel header, threshold plate, anchor bolts into CIP wall) | 1 | LS | 12000 |  | C10 | Supplemental to Item 35 (CIP wall cut $5,000). Vault door ~900 lbs requires steel lintel, sill plate, and frame anchoring into existing CIP wall.
7. BUILDING GENERAL - Whole-Building Systems & Code Compliance
47 | Bldg General | Adjust mechanical components first floor (HVAC diffusers, sprinklers, fire alarms) for ceiling removal | 1 | LS | 35000 |  | D30 | First floor mechanical adjustment: sprinkler heads, diffusers, FA devices
48 | Bldg General | Replace air-cooled chillers (2 EA) and chilled water circulating pumps (2 EA) - END OF SERVICE LIFE | 1 | LS | 500000 |  | D30 | CRITICAL: Chillers 12+ yrs past service life. 2x 100-150 ton chillers + 2x CW pumps + controls. VERIFY tonnage with FEAD mech engineer.
49 | Bldg General | Test, Adjust, Balance (TAB) all duct HVAC systems throughout facility (all 4 floors) | 1 | LS | 60000 |  | D30 | Full building TAB per AABC/NEBB standards. VERIFY if scope is first floor only or whole building.
50 | Bldg General | Replace 4 fire hose cabinets in new armory spaces (recessed, stainless, w/ hose/extinguisher) | 4 | EA | 2500 |  | D40 | Recessed FHC per NFPA 10, stainless steel finish
51 | Bldg General | Add supplemental water fountains in new OSS/Admin areas (4 EA) | 4 | EA | 5000 |  | D20 | Wall-mounted water fountains, plumbing connection, ADA compliance
8. BUILDING TELECOM - Telecom Room, OSP & ISP Cabling per UFC 3-580-01
52 | Telecom | Demo existing TR - remove all existing racks, cabling, equipment, flooring, paint | 1 | LS | 12000 |  | F20 | Full TR strip-out for renovation
53 | Telecom | Construct new TR: raised floor, racks, UPS, patch panels, grounding, EPO, fire suppression, HVAC | 1 | LS | 85000 |  | D50 | Full TR build-out per UFC 3-580-01 and MCIPAC G6 policy
54 | Telecom | Install OSP fiber optic cable from nearest demarcation point to building TR | 1 | LS | 15000 |  | D50 | OSP fiber, conduit, hand-holes, termination
55 | Telecom | Install ISP horizontal cabling - 28 drops to new armory spaces, admin, OSS areas | 28 | EA | 1200 |  | D50 | Cat6A or OM3 fiber per MCIPAC G6 policy, conduit, termination
56 | Telecom | Remove existing ISP cabling throughout first floor | 1 | LS | 4000 |  | F20 | Removal of legacy cabling, conduit, boxes per demo scope
9. EXTERIOR - Covered Overhangs, Pavilion, Site Work
57 | Exterior | Tree removal at new exterior concrete pad locations (6 EA) | 6 | EA | 1500 |  | G10 | Tree removal and disposal, stump grinding
58 | Exterior | Steel-frame covered overhang at issue windows - 3 locations | 3 | EA | 35000 |  | G20 | Steel-frame canopy structure, metal roofing, concrete footings, per location
59 | Exterior | New outdoor pavilion - steel frame, metal roof, concrete slab (approx 20'x40') | 1 | LS | 55000 |  | G20 | Steel-frame pavilion: columns, roof, 800 SF concrete slab, perimeter drainage
60 | Exterior | Site drainage improvements at new concrete pad locations | 1 | LS | 5000 |  | G20 | French drains or surface grading at pad locations
10. RESTROOMS & MISCELLANEOUS
61 | Rest/Misc | Public restroom: New fixtures (2 toilets, 2 sinks, accessories) for general use area | 1 | LS | 15000 |  | D20 | Replace fixtures, handles, accessories - ADA compliance check
62 | Rest/Misc | New security door/frame/lockset for exterior storage (1 EA) | 1 | EA | 6000 |  | C10 | Heavy-duty exterior security door with lockset and door closer
11. HAZARDOUS MATERIALS - Asbestos Mastic Abatement (Bhate Environmental Associates, 19 Nov 2001)
65 | Hazmat | Asbestos mastic abatement - OSS full-gut areas (mens locker ~398 SF, womens ~300 SF, sauna ~97 SF, steam ~124 SF); cove base/kickboard removal triggers abatement of underlying H3 ACM mastic (15% Chrysotile) | 234 | LF | 25 |  | F20 | Bhate Survey 19 Nov 2001, H3: 15% Chrysotile mastic under kickboard, 8,392 LF building-wide. Scope-limited to OSS gut rooms only. Perimeter est from room SF. FEAD ENV/IH to field-verify LF and unit cost before construction.
66 | Hazmat | Asbestos mastic abatement - armory bathroom VCT/CT renovation (11 bathrooms, ~1,650 SF total); floor tile and wall base removal at wall junctions triggers abatement of underlying H3 ACM mastic (15% Chrysotile) | 385 | LF | 25 |  | F20 | Bhate Survey 19 Nov 2001, H3. Armory scope Item 11: CT floor/wall removal in 11 baths. VCT/CT installation requires cove base removal at perimeter. Perimeter est: 11 baths x ~35 LF avg = 385 LF. FEAD ENV/IH to field-verify.
67 | Hazmat | Asbestos mastic abatement - gym conversion (VCT 1,749 SF, est. 168 LF perimeter) and laundry/admin conversion (VCT 300 SF, est. 70 LF perimeter); new VCT installation at wall base triggers abatement of underlying H3 ACM mastic | 238 | LF | 25 |  | F20 | Bhate Survey 19 Nov 2001, H3. Scope Items 3B (gym VCT) and 24 (laundry VCT) require base removal at wall perimeter. Combined perimeter est 238 LF. FEAD ENV/IH to field-verify.
TOTAL BASE DIRECT COST (FY24 CONUS)

## PARAMETERS
SCH-1024 ¦ COST ESTIMATE PARAMETERS ¦ LEVEL 3 ROM ¦ FY27 ¦ PAX ID 387356 ¦ Fi Web BU26PPE70M
PROJECT IDENTIFICATION
Estimate Title | SCH-1024 ¦ Repair MULTI PURPOSE BEQ/BOQ/CO HQS | Text | DD Form 1391 ¦ PAX ID 387356 ¦ Fi Web BU26PPE70M
Building / Installation | SCH-1024 ¦ Camp Schwab, Okinawa, Japan | Text | MCIPAC G-F PPE
Supported Units | 3rd Marine Logistics Group / III MEF | Text | Primary supported units
PAX ID | 387356 | ID | PAX System
Fi Web Project Number | BU26PPE70M | ID | Fi Web confirmed
iNFADS RPUID | 148675 | ID | iNFADS Real Property record
Primary Project CCN | 14345 | CCN | iNFADS CCN 14345
Total Building GSF | 84861 | SF | iNFADS confirmed
Plant Replacement Value (iNFADS) | 96523347 | $ | iNFADS confirmed; UFC 3-701-01 w/Ch 7
Estimate Date | 29 Apr 2026 | Date | Date of estimate production
Estimate Level | Level 3 ROM | Text | UFS 3-740-05 (2 Feb 2026); for information only
Delivery Method | Design-Build (DB) | Method | UFC 3-730-01 (2024)
COST INPUTS (yellow = user input; locked unless directed)
Base Year | 2024 | FY | FY24 CONUS base costs
Target Fiscal Year | 2027 | FY | FY27 construction start
Area Cost Factor (ACF) | 1.85 | Multiplier | UFC 3-701-01 w/Ch 7 (25 Jul 2025), Table 4-1 OCONUS Okinawa M67400-0004
Escalation Rate (annual) | 0.021 | % | OSD FY25 published rate, client confirmed
Escalation Years | 3 | Years | FY24 base to FY27 target
General Requirements | 0.1 | % | FSRM program-directed; UFS 3-740-05
PAX ASSOCIATED COSTS (informational; applied by PAX at submission)
Contingency | 10% | % | FSRM program-directed; PAX-applied to items subtotal
Supervision Inspection and Overhead (SIOH) | 8% | % | OCONUS FSRM customer-directed (8.0%); PAX-applied
Design-Build Design (DB) | 4% | % | UFC 3-730-01 (2024); PAX-applied
Planning and Design (P&D) | 6% | % | NON ADD; informational only; does not roll into TPC
DERIVED VALUES (live formulas; do not edit)
Compound Escalation Factor |  | Factor | (1 + escalation)^years
Base Direct Cost (FY24 CONUS) |  | $ | Sum of all scope items on SCOPE_DETAIL
Pre-Calibration Subtotal |  | $ | Base Direct x ACF x Escalation x (1 + General Requirements)
Locked Total Project Cost | 10413140 | $ | PAX-locked TPC; reconciliation target
Items Subtotal Target (PAX paste) |  | $ | Locked TPC / 1.23552 (1.10 x 1.08 x 1.04)
Cost Adjustment Factor |  | Factor | Items Subtotal Target / Pre-Calibration Subtotal; calibrates ROM chain to locked TPC
PLANNING RATES
JPY/USD Planning Rate | 150.4415 | Rate | FY26 budget planning rate; H.10 live rate at PAX submission
ACTIVE REFERENCES
MCO 11000.5 (03 Jun 2016) ¦ Real Property FSRM Program
MCO 11000.12 (08 Sep 2014) ¦ Real Property Facilities Manual
Consistency Review Board Guidelines (May 2024, REV #15) ¦ DD Form 1391 line-item sequencing
UFC 3-701-01 with Change 7 (25 Jul 2025) ¦ PUC, ACF, PRV authority
UFC 3-730-01 (2024) ¦ Design-Build contracting
UFS 3-740-05 (02 Feb 2026) ¦ Cost estimating ROM levels
JED Cost Estimating Guidance (Combined, Nov 2025)
Japan District Design Guide v9 (April 2025)
10 U.S.C. Section 2802 ¦ DoD 4270.5-M ¦ Classification of Work

## DD1391_BLOCK9
SCH-1024 ¦ DD FORM 1391 BLOCK 9 - PAX PASTE ¦ LEVEL 3 ROM ¦ FY27 ¦ PAX ID 387356 ¦ Fi Web BU26PPE70M
All amounts in $000s. Paste discipline rollups into PAX Block 9 items table; PAX-loaded Cont 10% / SIOH 8% / DB 4% render the printed Total Project Cost. P&D 6% NON ADD shown for visibility.
Cost Element | Amount ($000) | Notes / UNIFORMAT
B20 ¦ Exterior Enclosure |  | UNIFORMAT II Lv2 B20 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
C10 ¦ Interior Construction |  | UNIFORMAT II Lv2 C10 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
C30 ¦ Interior Finishes |  | UNIFORMAT II Lv2 C30 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
D20 ¦ Plumbing |  | UNIFORMAT II Lv2 D20 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
D30 ¦ HVAC / Mechanical |  | UNIFORMAT II Lv2 D30 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
D40 ¦ Fire Protection |  | UNIFORMAT II Lv2 D40 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
D50 ¦ Electrical / Communications |  | UNIFORMAT II Lv2 D50 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
E20 ¦ Furnishings |  | UNIFORMAT II Lv2 E20 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
F20 ¦ Selective Demolition |  | UNIFORMAT II Lv2 F20 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
G10 ¦ Site Preparation |  | UNIFORMAT II Lv2 G10 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
G20 ¦ Site Improvements |  | UNIFORMAT II Lv2 G20 rollup; absorbs base-cost adjustments via Cost Adjustment Factor
ITEMS SUBTOTAL (PAX Block 9 paste total) |  | Sum of discipline rollups; this is the value pasted into PAX items table
Contingency (10.0%) PAX-applied |  | 10% of items subtotal; FSRM program-directed
Total Contract Cost |  | Items subtotal x 1.10
SIOH (8.0%) PAX-applied |  | 8% of TCC; OCONUS FSRM customer-directed
Total Funded Cost |  | TCC x 1.08
DB Design (4.0%) PAX-applied |  | 4% of TFC; UFC 3-730-01 (2024)
TOTAL PROJECT COST |  | TFC x 1.04 = items subtotal x 1.23552
TOTAL PROJECT COST ($000 rounded) |  | Printed TPC on DD Form 1391 face
Planning and Design (6.0%) NON ADD |  | Informational; does not roll into TPC; PAX renders separately on form
Reconciliation (must equal 0) |  | Printed TPC ($000) minus Locked TPC ($000)
CLASSIFICATION OF WORK
Construction |  | 100% of Total Project Cost ¦ 10 U.S.C. Section 2802
Special Interest: Restoration and Modernization |  | 100% SRM ¦ MCO 11000.12 ¦ DoD 4270.5-M